## Allocation Summary
2006 | Summary of Cost Allocation Per Zone (in incremental ATRR)
| MW-Mi Impacts |  | No MW-Mi Impacts |  | 100% Zonal | Totals
ZONE | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | Zonal Allocations
CLECO | 0 | 0 | 0 | 0 | 0 | 0
SWPA | 0 | 0 | 0 | 0 | 0 | 0
AEP | 346343.9111 | 64743.3115 | 347537.1765 | 260205.7212 | 24137.822 | 1042967.9422
GRDA | 30139.5278 | 0 | 30243.3681 | 0 | 0 | 60382.8958
OKGE | 218461.3065 | 1037787.6243 | 219213.9755 | 0 | 39125.2537 | 1514588.1599
WFEC | 48717.0054 | 57320.8216 | 48884.851 | 0 | 16418.97 | 171341.6481
SPS | 177891.7296 | 38536.6697 | 178504.6235 | 1530398.1042 | 0 | 1925331.1271
MIDW | 11085.4181 | 0 | 11123.6109 | 0 | 0 | 22209.029
SUNF | 15025.0796 | 21696.2051 | 15076.8458 | 0 | 0 | 51798.1305
WESTAR | 178010.8876 | 1262825.4424 | 178624.192 | 759147.2018 | 6693.155 | 2385300.8788
WEPL | 18707.8067 | 26218.1091 | 18772.2611 | 0 | 0 | 63698.1769
MIPU | 62368.0443 | 62786.027 | 62582.9221 | 0 | 13112.475 | 200849.4684
KACP | 119038.8465 | 47730.2849 | 119448.9733 | 78918.9809 | 0 | 365137.0857
EMDE | 40603.09 | 0 | 40742.9806 | 0 | 0 | 81346.0707
SPRM | 23880.0088 | 0 | 23962.2831 | 0 | 0 | 47842.2919
TOTAL | 1290272.662 | 2619644.4956 | 1294718.0637 | 2628670.0081 | 99487.6757 | 7932792.9051
2007 | Summary of Cost Allocation Per Zone (in incremental ATRR)
| MW-Mi Impacts |  | No MW-Mi Impacts |  | 100% Zonal | Totals
ZONE | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | Zonal Allocations
CLECO | 0 | 0 | 0 | 0 | 0 | 0
SWPA | 0 | 0 | 0 | 0 | 0 | 0
AEP | 375396.5836 | 152226.6468 | 366251.351 | 172585.4273 | 47374.979 | 1113834.9878
GRDA | 32667.7484 | 536306.1363 | 31871.9123 | 0 | 0 | 600845.797
OKGE | 236786.6894 | 726315.2197 | 231018.2049 | 0 | 0 | 1194120.1141
WFEC | 52803.577 | 19202.0484 | 51517.2015 | 578148.4203 | 18243.3 | 719914.5472
SPS | 192813.9789 | 292934.9582 | 188116.7366 | 1007208.99 | 0 | 1681074.6637
MIDW | 12015.306 | 0 | 11722.5949 | 0 | 0 | 23737.9009
SUNF | 16285.4417 | 0 | 15888.7035 | 0 | 0 | 32174.1452
WESTAR | 192943.1323 | 484460.0024 | 188242.7437 | 739543.9069 | 0 | 1605189.7854
WEPL | 20277.0902 | 65045.1916 | 19783.1094 | 18962.6643 | 0 | 124068.0554
MIPU | 67599.7181 | 0 | 65952.886 | 29284.5275 | 0 | 162837.1316
KACP | 129024.2873 | 58352.2295 | 125881.0591 | 224484.6382 | 0 | 537742.2141
EMDE | 44009.0349 | 478980.6511 | 42936.9078 | 0 | 0 | 565926.5938
SPRM | 25883.1567 | 25567.3672 | 25252.6036 | 0 | 0 | 76703.1275
TOTAL | 1398505.7447 | 2839390.4513 | 1364436.0143 | 2770218.5745 | 65618.279 | 8438169.0637
2008 | Summary of Cost Allocation Per Zone (in incremental ATRR)
| MW-Mi Impacts |  | No MW-Mi Impacts |  | 100% Zonal | Totals
ZONE | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | Zonal Allocations
CLECO | 0 | 0 | 0 | 0 | 0 | 0
SWPA | 0 | 0 | 0 | 0 | 0 | 0
AEP | 826719.9949 | 876142.5724 | 258885.4454 | 211205.9425 | 35729.0203 | 2208682.9755
GRDA | 71942.7986 | 208404.2475 | 22528.7202 | 0 | 0 | 302875.7662
OKGE | 521465.2961 | 1594889.5328 | 163295.6458 | 17972.0532 | 0 | 2297622.528
WFEC | 116287.081 | 1018588.8107 | 36415.0292 | 91672.5825 | 0 | 1262963.5034
SPS | 424626.0584 | 110123.6382 | 132970.6635 | 1180672.7605 | 0 | 1848393.1205
MIDW | 26460.7995 | 0 | 8286.1379 | 52012.427 | 0 | 86759.3644
SUNF | 35864.7384 | 0 | 11230.9595 | 0 | 0 | 47095.6978
WESTAR | 424910.4875 | 497133.7522 | 133059.7318 | 216533.1259 | 0 | 1271637.0974
WEPL | 44655.3768 | 37906.1418 | 13983.7275 | 0 | 0 | 96545.2461
MIPU | 148871.9957 | 72521.8102 | 46618.9195 | 188065.2356 | 0 | 456077.9611
KACP | 284144.7226 | 149406.0746 | 88979.2596 | 0 | 0 | 522530.0569
EMDE | 96919.2335 | 1458505.784 | 30350.0328 | 0 | 3660.66 | 1589435.7102
SPRM | 57001.3797 | 229446.954 | 17849.8496 | 0 | 0 | 304298.1833
TOTAL | 3079869.9627 | 6253069.3183 | 964454.1223 | 1958134.1272 | 39389.6803 | 12294917.2108

## Projects Summary
| Number of Projects |  |  |  |  | E&C $ Millions |  |  |  |  | E&C $ Millions
ZONE | Direct Assigned | No MW-Mi | MW-Mi | Total | check | Direct Assigned | No MW-Mi | MW-Mi | Total | check | Direct Assigned | No MW-Mi | MW-Mi | Total
AEP | 8 | 9 | 2 | 19 | 19 | 595348 | 5336000 | 27627225 | 33558573 | 33558573 | 0.59535 | 5.336 | 27.6272 | 33.5586
GRDA | - | - | 1 | 1 | 1 | - | - | 1800000 | 1800000 | 1800000 | - | - | 1.8 | 1.8
OKGE | 3 | 2 | 5 | 10 | 10 | 175031.22 | 370000 | 15223277 | 15768308.22 | 15768308.22 | 0.17503 | 0.37 | 15.2233 | 15.7683
WFEC | 2 | 7 | 1 | 10 | 10 | 190000 | 5480000 | 12000000 | 17670000 | 17670000 | 0.19 | 5.48 | 12 | 17.67
SPS | - | 15 | 2 | 17 | 17 | - | 33225000 | 2000000 | 35225000 | 35225000 | - | 33.225 | 2 | 35.225
MIDW | - | 1 | - | 1 | 1 | - | 536000 | - | 536000 | 536000 | - | 0.536 | - | 0.536
SUNF | - | - | - | 0 | 0 | - | - | - | 0 | - | - | - | - | 0
WESTAR | 1 | 16 | 5 | 22 | 22 | 35000 | 13387000 | 15584000 | 29006000 | 29006000 | 0.035 | 13.387 | 15.584 | 29.006
WEPL | - | 1 | - | 1 | 1 | - | 148000 | - | 148000 | 148000 | - | 0.148 | - | 0.148
MIPU | 1 | 2 | 1 | 4 | 4 | 75000 | 1855500 | 536000 | 2466500 | 2466500 | 0.075 | 1.8555 | 0.536 | 2.4665
KACP | - | 3 | - | 3 | 3 | - | 2032200 | - | 2032200 | 2032200 | - | 2.0322 | - | 2.0322
EMDE | 1 | - | 2 | 3 | 3 | 20000 | - | 17272000 | 17292000 | 17292000 | 0.02 | - | 17.272 | 17.292
SPRM | - | - | - | 0 | 0 | - | - | - | 0 | - | - | - | - | 0
TOTAL | 16 | 56 | 19 | 91 |  | 1090379.22 | 62369700 | 92042502 | 155502581.22 |  | 1.0904 | 62.3697 | 92.0425 | 155.5026
|  |  | check | 91 | 91 |  |  |  |  | 155502581.22

## 100% Zonal E&C (ATRR)
| 2006 | 2007 | 2008
| 100% Zonal Allocation | 100% Zonal Allocation | 100% Zonal Allocation
ZONE | E&C in ATRR | E&C in ATRR | E&C in ATRR
AEP | 412504.57 | 1498747.0899 | 4133754.7703
GRDA | 0 | 342779.4 | 0
OKGE | 2167891.9313 | 849425.4 | 451536.66
WFEC | 16418.97 | 881151.39 | 2326020.75
SPS | 2284176.275 | 1837363 | 1762198.15
MIDW | 0 | 0 | 77630.488
SUNF | 0 | 0 | 0
WESTAR | 2827188.672 | 2033189.256 | 686526.47
WEPL | 0 | 28302.484 | 0
MIPU | 106822.963 | 43708.25 | 280694.3815
KACP | 117789.5238 | 335051.6988 | 0
EMDE | 0 | 588451.095 | 2576555.541
SPRM | 0 | 0 | 0
TOTAL | 7932792.9051 | 8438169.0637 | 12294917.2108

## 100% Zonal
Projects with 100% Zonal Allocation (<= $100k)
2006
|  | Area: | MIPU | OKGE | OKGE | WERE | AEPW | OKGE | WFEC | AEPW
|  | Project: | Line - Craig Interconnection | Line - Reno - Sunny Lane 69 kV | Line - Van Buren AVEC - VBI 69 kV | Line - Midwest Solvent Jct 1 - Atchison Jct 2 69 kV | Line - Lone Star South - Pittsburg 138 kV | Line - Brown Explorer Tap 138kV | Device - Rush Springs 69 kV | Line - Okmulgee - Weleetka 138 kV Ckt 1
|  | Cost: | 75000 | 100000 | 50000 | 35000 | 50000 | 25031.22 | 90000 | 84000
| TOTALS | FCR: | 0.17483 | 0.22353 | 0.22353 | 0.19123 | 0.18013 | 0.22353 | 0.18243 | 0.18013
ZONE | 100% Zonal Allocations | ZONE | 100% Zonal Allocations | 100% Zonal Allocations | 100% Zonal Allocations | 100% Zonal Allocations | 100% Zonal Allocations | 100% Zonal Allocations | 100% Zonal Allocations | 100% Zonal Allocations
CLECO |  | Area:: CLECO
SWPA |  | Area:: SWPA
AEP | 24137.822 | Area:: AEP; AEPW: 9006.65; AEPW: 15131.172
GRDA | 0 | Area:: GRDA
OKGE | 39125.2537 | Area:: OKGE; OKGE: 22353.3; OKGE: 11176.65; OKGE: 5595.3037
WFEC | 16418.97 | Area:: WFEC; WFEC: 16418.97
SPS | 0 | Area:: SPS
MIDW | 0 | Area:: MIDW
SUNF | 0 | Area:: SUNF
WESTAR | 6693.155 | Area:: WESTAR; WERE: 6693.155
WEPL | 0 | Area:: WEPL
MIPU | 13112.475 | Area:: MIPU; MIPU: 13112.475
KACP | 0 | Area:: KACP
EMDE | 0 | Area:: EMDE
SPRM | 0 | Area:: SPRM
TOTAL | 99487.6757 | TOTAL | 13112.475 | 22353.3 | 11176.65 | 6693.155 | 9006.65 | 5595.3037 | 16418.97 | 15131.172
| 99487.6757 |  | 13112.475 | 22353.3 | 11176.65 | 6693.155 | 9006.65 | 5595.3037 | 16418.97 | 15131.172
2007
|  | Area: | AEPW | AEPW | AEPW | WFEC
|  | Project: | Line - 53rd & Garnett N. Tap - Tulsa Southeast 138 kV | Line - Knox Lee - Oak Hill #2 138 kV | Line - Elk City - Elk City 69 kV | Device - Snyder
|  | Cost: | 63000 | 100000 | 100000 | 100000
| TOTALS | Area:: FCR:; MIPU: 0.18013; OKGE: 0.18013; OKGE: 0.18013; WERE: 0.18243
ZONE | 100% Zonal Allocations | Area:: ZONE; MIPU: 100% Zonal Allocations; OKGE: 100% Zonal Allocations; OKGE: 100% Zonal Allocations; WERE: 100% Zonal Allocations
CLECO |  | Area:: CLECO
SWPA |  | Area:: SWPA
AEP | 47374.979 | Area:: AEP; MIPU: 11348.379; OKGE: 18013.3; OKGE: 18013.3
GRDA | 0 | Area:: GRDA
OKGE | 0 | Area:: OKGE
WFEC | 18243.3 | Area:: WFEC; WERE: 18243.3
SPS | 0 | Area:: SPS
MIDW | 0 | Area:: MIDW
SUNF | 0 | Area:: SUNF
WESTAR | 0 | Area:: WESTAR
WEPL | 0 | Area:: WEPL
MIPU | 0 | Area:: MIPU
KACP | 0 | Area:: KACP
EMDE | 0 | Area:: EMDE
SPRM | 0 | Area:: SPRM
TOTAL | 65618.279 | Area:: TOTAL; MIPU: 11348.379; OKGE: 18013.3; OKGE: 18013.3; WERE: 18243.3
| 65618.279 | MIPU: 11348.379; OKGE: 18013.3; OKGE: 18013.3; WERE: 18243.3
2008
|  | Area: | AEPW | EMDE | AEPW | AEPW
|  | Project: | Line - Bann - Kings Highway 69 kV | Line - Sub 167 - Riverton - Sub 406 - Riverton S | Line - Cache - Snyder 138kV | Line - NW Henderson - Oak Hill 138 kV
|  | Cost: | 50000 | 20000 | 73348 | 75000
| TOTALS | Area:: FCR:; MIPU: 0.18013; OKGE: 0.18303; OKGE: 0.18013; WERE: 0.18013
ZONE | 100% Zonal Allocations | Area:: ZONE; MIPU: 100% Zonal Allocations; OKGE: 100% Zonal Allocations; OKGE: 100% Zonal Allocations; WERE: 100% Zonal Allocations
CLECO |  | Area:: CLECO
SWPA |  | Area:: SWPA
AEP | 35729.0203 | Area:: AEP; MIPU: 9006.65; OKGE: 13212.3953; WERE: 13509.975
GRDA | 0 | Area:: GRDA
OKGE | 0 | Area:: OKGE
WFEC | 0 | Area:: WFEC
SPS | 0 | Area:: SPS
MIDW | 0 | Area:: MIDW
SUNF | 0 | Area:: SUNF
WESTAR | 0 | Area:: WESTAR
WEPL | 0 | Area:: WEPL
MIPU | 0 | Area:: MIPU
KACP | 0 | Area:: KACP
EMDE | 3660.66 | Area:: EMDE; OKGE: 3660.66
SPRM | 0 | Area:: SPRM
TOTAL | 39389.6803 | Area:: TOTAL; MIPU: 9006.65; OKGE: 3660.66; OKGE: 13212.3953; WERE: 13509.975
| 39389.6803 | MIPU: 9006.65; OKGE: 3660.66; OKGE: 13212.3953; WERE: 13509.975

## No MW-mi Allocations
Projects with No Mw-mi Impact
2006
[5 empty] | Area: | AEPW | Area: | AEPW | Area: | AEPW | Area: | AEPW | Area: | KCPL | Area: | SPS | Area: | SPS | Area: | SPS | Area: | SPS | Area: | SPS | Area: | SPS | Area: | WERE | Area: | WERE | Area: | WERE | Area: | WERE | Area: | WERE
[5 empty] | Project: | Line - Tontitown - Elm Springs REC 161 kV | Project: | Device - Arsenal Hill | Project: | Device - Catoosa | Project: | Line - Carthage REC - Carthage T 138 kV | Project: | Line - Tomahawk - Bendix 161 kV | Project: | XFR - Bailey Co 115/69 kV | Project: | XFR - Denver City 115/69 kV | Project: | XFR - Kress 115/69 kV | Project: | XFR - Hockley 115/69 kV | Project: | XFR - Terry Co 115/69 kV | Project: | XFR - Hale Co 115/69 kV | Project: | Line - Circle - Hutchinson Energy Center 115 kV | Project: | Device - Clearwater | Project: | Device - UDALL 2 | Project: | Multi - HEC - 43rd & Lorraine - Tower 33 69 kV | Project: | Line - Cities Service - 3rd & VanBuren 69 kV
[5 empty] | Cost: | 640000 | Cost: | 432000 | Cost: | 394000 | Cost: | 690000 | Cost: | 528600 | Cost: | 2200000 | Cost: | 2200000 | Cost: | 1250000 | Cost: | 2750000 | Cost: | 2375000 | Cost: | 2900000 | Cost: | 300000 | Cost: | 1000000 | Cost: | 525000 | Cost: | 2400000 | Cost: | 1700000
[5 empty] | FCR: | 0.18013 | FCR: | 0.18013 | FCR: | 0.18013 | FCR: | 0.18013 | FCR: | 0.22283 | FCR: | 0.16703 | FCR: | 0.16703 | FCR: | 0.16703 | FCR: | 0.16703 | FCR: | 0.16703 | FCR: | 0.16703 | FCR: | 0.19123 | FCR: | 0.19123 | FCR: | 0.19123 | FCR: | 0.19123 | FCR: | 0.19123 | [18 empty] | 100% Zonal E&C (in ATRR)
ZONE | Residential Load Shares | 33% Regional Allocations | 67% MW-mi Allocations | ZONE | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | [18 empty] | ZONE | 100% Zonal
CLECO |  |  |  | CLECO | [50 empty] | CLECO | -
SWPA |  |  |  | SWPA | [50 empty] | SWPA | -
AEP | 26.84% | 347537.1765 | 260205.7212 | AEP | 10212.0576 | 77241.0304 | 6893.1389 | 52137.6955 | 6286.798 | 47551.5093 | 11009.8746 | 83275.4859 | 10433.8999 |  | 32551.0471 |  | 32551.0471 |  | 18494.9131 |  | 40688.8089 |  | 35140.3349 |  | 42908.1984 |  | 5081.8764 |  | 16939.5878 |  | 8893.2836 |  | 40655.0108 |  | 28797.2993 | [19 empty] | AEP | 388366.748
GRDA | 2.336% | 30243.3681 | 0 | GRDA | Area:: 888.6733; Area:: 599.8545; Area:: 547.0895; Area:: 958.1009; Area:: 907.9785; Area:: 2832.6561; Area:: 2832.6561; Area:: 1609.4637; Area:: 3540.8201; Area:: 3057.981; Area:: 3733.9557; Area:: 442.2349; Area:: 1474.1162; Area:: 773.911; Area:: 3537.8789; Area:: 2505.9976 | [18 empty] | GRDA
OKGE | 16.93% | 219213.9755 | 0 | OKGE | Area:: 6441.3994; Area:: 4347.9446; Area:: 3965.4865; Area:: 6944.6337; Area:: 6581.3295; Area:: 20532.032; Area:: 20532.032; Area:: 11665.9273; Area:: 25665.04; Area:: 22165.2618; Area:: 27064.9513; Area:: 3205.4652; Area:: 10684.8839; Area:: 5609.5641; Area:: 25643.7214; Area:: 18164.3027 | [18 empty] | OKGE
WFEC | 3.776% | 48884.851 | 0 | WFEC | Area:: 1436.436; Area:: 969.5943; Area:: 884.3059; Area:: 1548.6576; Area:: 1467.6405; Area:: 4578.6557; Area:: 4578.6557; Area:: 2601.5089; Area:: 5723.3197; Area:: 4942.867; Area:: 6035.5007; Area:: 714.8207; Area:: 2382.7357; Area:: 1250.9362; Area:: 5718.5656; Area:: 4050.6506 | [18 empty] | WFEC
SPS | 13.79% | 178504.6235 | 1530398.1042 | SPS | 5245.1928 |  | 3540.5052 |  | 3229.0718 |  | 5654.9735 |  | 5359.1371 |  | 16719.1103 | 246206.642 | 16719.1103 | 246206.642 | 9499.4945 | 139890.1375 | 20898.8879 | 307758.3025 | 18049.0396 | 265791.2612 | 22038.8273 | 324545.119 | 2610.191 |  | 8700.6368 |  | 4567.8343 |  | 20881.5283 |  | 14791.0826 | [19 empty] | SPS | 2284176.275
MIDW | 0.8592% | 11123.6109 | 0 | MIDW | Area:: 326.857; Area:: 220.6285; Area:: 201.2213; Area:: 352.3927; Area:: 333.9575; Area:: 1041.8603; Area:: 1041.8603; Area:: 591.9661; Area:: 1302.3254; Area:: 1124.7355; Area:: 1373.3613; Area:: 162.6554; Area:: 542.1848; Area:: 284.647; Area:: 1301.2436; Area:: 921.7142 | [18 empty] | MIDW
SUNF | 1.164% | 15076.8458 | 0 | SUNF | Area:: 443.0191; Area:: 299.0379; Area:: 272.7337; Area:: 477.63; Area:: 452.6431; Area:: 1412.1284; Area:: 1412.1284; Area:: 802.3457; Area:: 1765.1605; Area:: 1524.4568; Area:: 1861.442; Area:: 220.4618; Area:: 734.8726; Area:: 385.8081; Area:: 1763.6943; Area:: 1249.2834 | [18 empty] | SUNF
WESTAR | 13.8% | 178624.192 | 759147.2018 | WESTAR | 5248.7062 |  | 3542.8767 |  | 3231.2348 |  | 5658.7614 |  | 5362.7268 |  | 16730.3094 |  | 16730.3094 |  | 9505.8576 |  | 20912.8867 |  | 18061.1294 |  | 22053.5896 |  | 2611.9394 | 38437.833 | 8706.4648 | 128126.11 | 4570.894 | 67266.2078 | 20895.5155 | 307502.664 | 14800.9901 | 217814.387 | [18 empty] | WESTAR | 1133055.525
WEPL | 1.45% | 18772.2611 | 0 | WEPL | Area:: 551.6055; Area:: 372.3337; Area:: 339.5821; Area:: 594.6997; Area:: 563.5883; Area:: 1758.2486; Area:: 1758.2486; Area:: 999.0049; Area:: 2197.8108; Area:: 1898.1093; Area:: 2317.6913; Area:: 274.4981; Area:: 914.9938; Area:: 480.3718; Area:: 2195.9851; Area:: 1555.4895 | [18 empty] | WEPL
MIPU | 4.834% | 62582.9221 | 0 | MIPU | Area:: 1838.9411; Area:: 1241.2853; Area:: 1132.0981; Area:: 1982.6084; Area:: 1878.8895; Area:: 5861.6453; Area:: 5861.6453; Area:: 3330.4803; Area:: 7327.0566; Area:: 6327.9125; Area:: 7726.7142; Area:: 915.1213; Area:: 3050.4043; Area:: 1601.4623; Area:: 7320.9704; Area:: 5185.6874 | [18 empty] | MIPU
KACP | 9.226% | 119448.9733 | 78918.9809 | KACP | Area:: 3509.8973; Area:: 2369.1807; Area:: 2160.7805; Area:: 3784.108; Area:: 3586.1448; KCPL: 78918.9809; Area:: 11187.8366; Area:: 11187.8366; Area:: 6356.7254; Area:: 13984.7958; Area:: 12077.7782; Area:: 14747.6028; Area:: 1746.6474; Area:: 5822.1581; Area:: 3056.633; Area:: 13973.1794; Area:: 9897.6687 | [18 empty] | KACP | 117789.5238
EMDE | 3.147% | 40742.9806 | 0 | EMDE | Area:: 1197.1947; Area:: 808.1064; Area:: 737.023; Area:: 1290.7255; Area:: 1223.202; Area:: 3816.0714; Area:: 3816.0714; Area:: 2168.2224; Area:: 4770.0893; Area:: 4119.6225; Area:: 5030.2759; Area:: 595.7659; Area:: 1985.8862; Area:: 1042.5903; Area:: 4766.127; Area:: 3376.0066 | [18 empty] | EMDE
SPRM | 1.851% | 23962.2831 | 0 | SPRM | Area:: 704.1095; Area:: 475.2739; Area:: 433.4674; Area:: 759.118; Area:: 719.4052; Area:: 2244.3567; Area:: 2244.3567; Area:: 1275.2027; Area:: 2805.4459; Area:: 2422.8851; Area:: 2958.4703; Area:: 350.3894; Area:: 1167.9648; Area:: 613.1815; Area:: 2803.1156; Area:: 1985.5402 | [18 empty] | SPRM
TOTAL | 100% | 1294718.0637 | 2628670.0081 | TOTAL | 38044.0896 | 77241.0304 | 25679.7605 | 52137.6955 | 23420.8927 | 47551.5093 | 41016.2841 | 83275.4859 | 38870.5429 | 78918.9809 | 121265.958 | 246206.642 | 121265.958 | 246206.642 | 68901.1125 | 139890.1375 | 151582.4475 | 307758.3025 | 130912.1137 | 265791.2612 | 159850.581 | 324545.119 | 18932.067 | 38437.833 | 63106.89 | 128126.11 | 33131.1172 | 67266.2078 | 151456.536 | 307502.664 | 107281.713 | 217814.387 | [18 empty] | TOTAL | 3923388.0718
|  | 1294718.0637 | 2628670.0081 |  | 38044.0896 | 77241.0304 | 25679.7605 | 52137.6955 | 23420.8927 | 47551.5093 | 41016.2841 | 83275.4859 | 38870.5429 | 78918.9809 | 121265.958 | 246206.642 | 121265.958 | 246206.642 | 68901.1125 | 139890.1375 | 151582.4475 | 307758.3025 | 130912.1137 | 265791.2612 | 159850.581 | 324545.119 | 18932.067 | 38437.833 | 63106.89 | 128126.11 | 33131.1173 | 67266.2078 | 151456.536 | 307502.664 | 107281.713 | 217814.387 | [19 empty] | 3923388.0718
2007
[5 empty] | Area: | AEPW | Area: | KACP | Area: | KACP | Area: | WERE | Area: | WERE | Area: | WERE | Area: | AEPW | Area: | AEPW | Area: | AEPW | Area: | SPS | Area: | SPS | Area: | SPS | Area: | WEPL | Area: | WERE | Area: | WERE | Area: | WERE | Area: | WFEC | Area: | WFEC | Area: | WFEC | Area: | WFEC | Area: | WFEC | Area: | WFEC | Area: | MIPU | Area: | SPS | Area: | WERE
[5 empty] | Project: | Line - South Shreveport - SW Shreveport 138 kV | Project: | Device - South Waverly | Project: | Line - Stilwell - Antioch 161 kV | Project: | Device - Parsons | Project: | Device - Parsons | Project: | Device - Nortonville 69 kV Cap | Project: | Line - Porter Hill - Elgin Junction | Project: | Device - Broken Arrow Water | Project: | Device - Hobart | Project: | XFR - Carlsbad Int 115 kV - Carlsbad Int 69 kV | Project: | XFR - Gaines Co Int 69 kV - Gaines Co Int 115 kV | Project: | Device - San Andress Sub | Project: | GREENSBURG - JUDSON LARGE 115KV CKT 1 | Project: | Line - Golden Plain - Gatz 69 kV Rebuild | Project: | Line - Hesston - Golden Plain 69 kV Rebuild | Project: | Line - Murry Gill Energy Center - MacArthur 69 kV | Project: | Line - ACME - W Norman 69 kV | Project: | Device - Cashion 69 kV | Project: | Device - Comanche | Project: | Device - Pink Southwest 138 kV | Project: | Line - Bradley - Rush Springs 69 kV | Project: | Line - Elmore - Wallville 69 kV | Project: | Line - Lake Road to Industrial Park 161 kV | Project: | XFR - Artesia 115/69 kV | Project: | XFR - County Line 115/69 kV
[5 empty] | Cost: | 130000 | Cost: | 611000 | Cost: | 892600 | Cost: | 1000000 | Cost: | 525000 | Cost: | 564000 | Cost: | 200000 | Cost: | 550000 | Cost: | 550000 | Cost: | 2750000 | Cost: | 2750000 | Cost: | 750000 | Cost: | 148000 | Cost: | 590000 | Cost: | 1250000 | Cost: | 143000 | Cost: | 912000 | Cost: | 108000 | Cost: | 350000 | Cost: | 216000 | Cost: | 1656000 | Cost: | 1488000 | Cost: | 250000 | Cost: | 2750000 | Cost: | 1700000
|  | TOTALS |  |  | FCR: | 0.18013 | FCR: | 0.22283 | FCR: | 0.22283 | FCR: | 0.19123 | FCR: | 0.19123 | FCR: | 0.19123 | FCR: | 0.18013 | FCR: | 0.18013 | FCR: | 0.18013 | FCR: | 0.16703 | FCR: | 0.16703 | FCR: | 0.16703 | FCR: | 0.19123 | FCR: | 0.19123 | FCR: | 0.19123 | FCR: | 0.19123 | FCR: | 0.18243 | FCR: | 0.18243 | FCR: | 0.18243 | FCR: | 0.18243 | FCR: | 0.18243 | FCR: | 0.18243 | FCR: | 0.17483 | FCR: | 0.16703 | FCR: | 0.19123 | 100% Zonal E&C (in ATRR)
ZONE | Residential Load Shares | 33% Regional Allocations | 67% MW-mi Allocations | ZONE | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | ZONE | 100% Zonal
CLECO |  |  |  | CLECO | [50 empty] | CLECO | - | bar: Area: to WERE
SWPA |  |  |  | SWPA | [50 empty] | SWPA | - | bar: Area: to WERE
AEP | 26.84% | 366251.351 | 172585.4273 | AEP | Area:: 2074.3242; AEPW: 15689.5843; Area:: 12060.3724; Area:: 17618.8026; Area:: 16939.5878; Area:: 8893.2836; Area:: 9553.9275; Area:: 3191.268; AEPW: 24137.822; Area:: 8775.987; AEPW: 66379.0105; Area:: 8775.987; AEPW: 66379.0105; Area:: 40688.8089; Area:: 40688.8089; Area:: 11096.9479; Area:: 2507.059; Area:: 9994.3568; Area:: 21174.4848; Area:: 2422.3611; Area:: 14737.9894; Area:: 1745.2882; Area:: 5656.0266; Area:: 3490.5764; Area:: 26761.086; Area:: 24046.1932; Area:: 3871.7153; Area:: 40688.8089; Area:: 28797.2993 | AEP | 257590.19
GRDA | 2.336% | 31871.9123 | 0 | GRDA | Area:: 180.5118; Area:: 1049.5173; Area:: 1533.2228; Area:: 1474.1162; Area:: 773.911; Area:: 831.4015; Area:: 277.7104; Area:: 763.7036; Area:: 763.7036; Area:: 3540.8201; Area:: 3540.8201; Area:: 965.6782; Area:: 218.1692; Area:: 869.7286; Area:: 1842.6453; Area:: 210.7986; Area:: 1282.5288; Area:: 151.8784; Area:: 492.1986; Area:: 303.7568; Area:: 2328.8023; Area:: 2092.547; Area:: 336.9243; Area:: 3540.8201; Area:: 2505.9976 | GRDA
OKGE | 16.93% | 231018.2049 | 0 | OKGE | Area:: 1308.4092; Area:: 7607.25; Area:: 11113.3082; Area:: 10684.8839; Area:: 5609.5641; Area:: 6026.2745; Area:: 2012.9373; Area:: 5535.5776; Area:: 5535.5776; Area:: 25665.04; Area:: 25665.04; Area:: 6999.5564; Area:: 1581.3628; Area:: 6304.0815; Area:: 13356.1049; Area:: 1527.9384; Area:: 9296.1947; Area:: 1100.8652; Area:: 3567.6186; Area:: 2201.7303; Area:: 16879.9324; Area:: 15167.4755; Area:: 2442.1391; Area:: 25665.04; Area:: 18164.3027 | OKGE
WFEC | 3.776% | 51517.2015 | 578148.4203 | WFEC | 291.7761 |  | 1696.4214 |  | 2478.2746 |  | 2382.7357 |  | 1250.9362 |  | 1343.8629 |  | 448.8863 |  | 1234.4372 |  | 1234.4372 |  | 5723.3197 |  | 5723.3197 |  | 1560.9054 |  | 352.6449 |  | 1405.814 |  | 2978.4196 |  | 340.7312 |  | 2073.0571 | 111473.8603 | 245.4936 | 13200.8519 | 795.5811 | 42780.5385 | 490.9872 | 26401.7038 | 3764.2353 | 202413.0622 | 3382.3563 | 181878.4037 | 544.5985 |  | 5723.3197 |  | 4050.6506 |  | WFEC | 862908.09
SPS | 13.79% | 188116.7366 | 1007208.99 | SPS | Area:: 1065.4298; Area:: 6194.538; Area:: 9049.5002; Area:: 8700.6368; Area:: 4567.8343; Area:: 4907.1592; Area:: 1639.1228; Area:: 4507.5876; Area:: 4507.5876; Area:: 20898.8879; SPS: 307758.3025; Area:: 20898.8879; SPS: 307758.3025; Area:: 5699.6967; SPS: 83934.0825; Area:: 1287.6942; Area:: 5133.3757; Area:: 10875.796; Area:: 1244.1911; Area:: 7569.8355; Area:: 896.4279; Area:: 2905.0904; Area:: 1792.8558; Area:: 13745.2276; Area:: 12350.7842; Area:: 1988.6192; Area:: 20898.8879; SPS: 307758.3025; Area:: 14791.0826 | SPS | 1503297
MIDW | 0.8592% | 11722.5949 | 0 | MIDW | Area:: 66.3928; Area:: 386.0159; Area:: 563.9244; Area:: 542.1848; Area:: 284.647; Area:: 305.7922; Area:: 102.1428; Area:: 280.8927; Area:: 280.8927; Area:: 1302.3254; Area:: 1302.3254; Area:: 355.1796; Area:: 80.2434; Area:: 319.889; Area:: 677.731; Area:: 77.5324; Area:: 471.7183; Area:: 55.8614; Area:: 181.0323; Area:: 111.7228; Area:: 856.5412; Area:: 769.6457; Area:: 123.9219; Area:: 1302.3254; Area:: 921.7142 | MIDW
SUNF | 1.164% | 15888.7035 | 0 | SUNF | Area:: 89.9883; Area:: 523.2027; Area:: 764.3383; Area:: 734.8726; Area:: 385.8081; Area:: 414.4682; Area:: 138.4435; Area:: 380.7196; Area:: 380.7196; Area:: 1765.1605; Area:: 1765.1605; Area:: 481.4074; Area:: 108.7611; Area:: 433.5748; Area:: 918.5908; Area:: 105.0868; Area:: 639.3629; Area:: 75.714; Area:: 245.3696; Area:: 151.4281; Area:: 1160.9485; Area:: 1043.1711; Area:: 167.9626; Area:: 1765.1605; Area:: 1249.2834 | SUNF
WESTAR | 13.8% | 188242.7437 | 739543.9069 | WESTAR | 1066.1435 |  | 6198.6873 |  | 9055.5618 |  | 8706.4648 | 128126.11 | 4570.894 | 67266.2078 | 4910.4461 | 72263.126 | 1640.2207 |  | 4510.6069 |  | 4510.6069 |  | 20912.8867 |  | 20912.8867 |  | 5703.5146 |  | 1288.5568 |  | 5136.8142 | 75594.4049 | 10883.081 | 160157.6375 | 1245.0245 | 18322.0337 | 7574.906 |  | 897.0283 |  | 2907.0363 |  | 1794.0567 |  | 13754.4346 |  | 12359.0572 |  | 1989.9512 |  | 20912.8867 |  | 14800.9901 | 217814.387 | WESTAR | 1103796.876
WEPL | 1.45% | 19783.1094 | 18962.6643 | WEPL | Area:: 112.0449; Area:: 651.4424; Area:: 951.6817; Area:: 914.9938; Area:: 480.3718; Area:: 516.0565; Area:: 172.3767; Area:: 474.036; Area:: 474.036; Area:: 2197.8108; Area:: 2197.8108; Area:: 599.4029; Area:: 135.4191; WEPL: 18962.6643; Area:: 539.8463; Area:: 1143.7423; Area:: 130.8441; Area:: 796.0742; Area:: 94.2719; Area:: 305.5109; Area:: 188.5439; Area:: 1445.5032; Area:: 1298.8579; Area:: 209.1312; Area:: 2197.8108; Area:: 1555.4895 | WEPL | 28302.484
MIPU | 4.834% | 65952.886 | 29284.5275 | MIPU | Area:: 373.5349; Area:: 2171.7773; Area:: 3172.7143; Area:: 3050.4043; Area:: 1601.4623; Area:: 1720.428; Area:: 574.6691; Area:: 1580.34; Area:: 1580.34; Area:: 7327.0566; Area:: 7327.0566; Area:: 1998.2882; Area:: 451.4598; Area:: 1799.7386; Area:: 3813.0054; Area:: 436.2078; Area:: 2653.9504; Area:: 314.2836; Area:: 1018.5117; Area:: 628.5672; Area:: 4819.0153; Area:: 4330.1297; Area:: 697.201; MIPU: 29284.5275; Area:: 7327.0566; Area:: 5185.6874 | MIPU | 43708.25
KACP | 9.226% | 125881.0591 | 224484.6382 | KACP | Area:: 712.9479; Area:: 4145.1655; KACP: 91221.1452; Area:: 6055.6051; KACP: 133263.493; Area:: 5822.1581; Area:: 3056.633; Area:: 3283.6972; Area:: 1096.8429; Area:: 3016.318; Area:: 3016.318; Area:: 13984.7958; Area:: 13984.7958; Area:: 3814.0352; Area:: 861.6794; Area:: 3435.0733; Area:: 7277.6976; Area:: 832.5686; Area:: 5065.4659; Area:: 599.8578; Area:: 1943.9836; Area:: 1199.7156; Area:: 9197.8196; Area:: 8264.7074; Area:: 1330.7135; Area:: 13984.7958; Area:: 9897.6687 | KACP | 335051.6988
EMDE | 3.147% | 42936.9078 | 0 | EMDE | Area:: 243.1802; Area:: 1413.879; Area:: 2065.5129; Area:: 1985.8862; Area:: 1042.5903; Area:: 1120.0398; Area:: 374.1233; Area:: 1028.8392; Area:: 1028.8392; Area:: 4770.0893; Area:: 4770.0893; Area:: 1300.9334; Area:: 293.9112; Area:: 1171.6729; Area:: 2482.3578; Area:: 283.9817; Area:: 1727.7853; Area:: 204.6062; Area:: 663.0755; Area:: 409.2123; Area:: 3137.2943; Area:: 2819.0181; Area:: 453.8945; Area:: 4770.0893; Area:: 3376.0066 | EMDE
SPRM | 1.851% | 25252.6036 | 0 | SPRM | Area:: 143.0222; Area:: 831.5486; Area:: 1214.7959; Area:: 1167.9648; Area:: 613.1815; Area:: 658.7322; Area:: 220.0342; Area:: 605.0941; Area:: 605.0941; Area:: 2805.4459; Area:: 2805.4459; Area:: 765.1216; Area:: 172.8588; Area:: 689.0992; Area:: 1459.956; Area:: 167.019; Area:: 1016.1672; Area:: 120.3356; Area:: 389.9764; Area:: 240.6712; Area:: 1845.1457; Area:: 1657.957; Area:: 266.9503; Area:: 2805.4459; Area:: 1985.5402 | SPRM
TOTAL | 100% | 1364436.0143 | 2770218.5745 | TOTAL | 7727.7057 | 15689.5843 | 44929.8178 | 91221.1452 | 65637.2428 | 133263.493 | 63106.89 | 128126.11 | 33131.1172 | 67266.2078 | 35592.286 | 72263.126 | 11888.778 | 24137.822 | 32694.1395 | 66379.0105 | 32694.1395 | 66379.0105 | 151582.4475 | 307758.3025 | 151582.4475 | 307758.3025 | 41340.6675 | 83934.0825 | 9339.8197 | 18962.6643 | 37233.0651 | 75594.4049 | 78883.6125 | 160157.6375 | 9024.2853 | 18322.0337 | 54905.0357 | 111473.8603 | 6501.9121 | 13200.8519 | 21071.0115 | 42780.5385 | 13003.8242 | 26401.7038 | 99695.9858 | 202413.0622 | 89581.9003 | 181878.4037 | 14423.7225 | 29284.5275 | 151582.4475 | 307758.3025 | 107281.713 | 217814.387 | TOTAL | 4134654.5888
|  | 1364436.0143 | 2770218.5745 |  | 7727.7057 | 15689.5843 | 44929.8178 | 91221.1452 | 65637.2428 | 133263.493 | 63106.89 | 128126.11 | 33131.1173 | 67266.2078 | 35592.286 | 72263.126 | 11888.778 | 24137.822 | 32694.1395 | 66379.0105 | 32694.1395 | 66379.0105 | 151582.4475 | 307758.3025 | 151582.4475 | 307758.3025 | 41340.6675 | 83934.0825 | 9339.8197 | 18962.6643 | 37233.0651 | 75594.4049 | 78883.6125 | 160157.6375 | 9024.2853 | 18322.0337 | 54905.0357 | 111473.8603 | 6501.9121 | 13200.8519 | 21071.0115 | 42780.5385 | 13003.8242 | 26401.7038 | 99695.9858 | 202413.0622 | 89581.9003 | 181878.4037 | 14423.7225 | 29284.5275 | 151582.4475 | 307758.3025 | 107281.713 | 217814.387 |  | 4134654.5888
2008
[5 empty] | Area: | AEPW | Area: | SPS | Area: | SPS | Area: | SPS | Area: | WERE | Area: | WERE | Area: | WERE | Area: | MIDW | Area: | MIPU | Area: | SPS | Area: | SPS | Area: | WERE | Area: | OKGE | Area: | WFEC
[5 empty] | Project: | Line - Northwest Texarkana - Alumax Tap | Project: | XFR - Lubbock East 115/69 kV | Project: | XFR - Mustang Sta N. 115 kV - Mustang Sta 230 kV | Project: | Device - Bowers | Project: | Line - Coffeyville - CRA 69 kV Rebuild | Project: | Line - Dearing - Coffeyville 69 kV Rebuild | Project: | Device - Sunset 69 kV Cap | Project: | Multi - Knoll - Hays - Vine 115 kV | Project: | Line - Blue Springs - Duncan Road 161 kV | Project: | XFR - Cochran 115/69 kV | Project: | XFR - NE Hereford 115/69 kV | Project: | Device - 3rd & VanBuren 115 kV | Project: | Line - Wind Farm - Mooreland 138 kV | Project: | Line - Wind Farm - Mooreland 138 kV
[5 empty] | Cost: | 1750000 | Cost: | 2750000 | Cost: | 3000000 | Cost: | 300000 | Cost: | 250000 | Cost: | 390000 | Cost: | 550000 | Cost: | 536000 | Cost: | 1605500 | Cost: | 2750000 | Cost: | 1750000 | Cost: | 500000 | Cost: | 120000 | Cost: | 750000
|  | TOTALS |  |  | FCR: | 0.18013 | FCR: | 0.16703 | FCR: | 0.16703 | FCR: | 0.16703 | FCR: | 0.19123 | FCR: | 0.19123 | FCR: | 0.19123 | FCR: | 0.14483 | FCR: | 0.17483 | FCR: | 0.16703 | FCR: | 0.16703 | FCR: | 0.19123 | FCR: | 0.22353 | FCR: | 0.18243 | [22 empty] | 100% Zonal E&C (in ATRR)
ZONE | Residential Load Shares | 33% Regional Allocations | 67% MW-mi Allocations | ZONE | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | [22 empty] | ZONE | 100% Zonal
CLECO |  |  |  | CLECO | [50 empty] | CLECO | -
SWPA |  |  |  | SWPA | [50 empty] | SWPA | -
AEP | 26.84% | 258885.4454 | 211205.9425 | AEP | Area:: 27923.5951; AEPW: 211205.9425; Area:: 40688.8089; Area:: 44387.7915; Area:: 4438.7791; Area:: 4234.897; Area:: 6606.4393; Area:: 9316.7733; Area:: 6876.5771; Area:: 24864.1559; Area:: 40688.8089; Area:: 25892.8784; Area:: 8469.7939; Area:: 2376.09; Area:: 12120.0571 | [22 empty] | AEP | 315232.75
GRDA | 2.336% | 22528.7202 | 0 | GRDA | Area:: 2429.9661; Area:: 3540.8201; Area:: 3862.7128; Area:: 386.2713; Area:: 368.5291; Area:: 574.9053; Area:: 810.7639; Area:: 598.4133; Area:: 2163.7277; Area:: 3540.8201; Area:: 2253.2492; Area:: 737.0581; Area:: 206.772; Area:: 1054.7112 | [22 empty] | GRDA
OKGE | 16.93% | 163295.6458 | 17972.0532 | OKGE | Area:: 17613.2014; Area:: 25665.04; Area:: 27998.2255; Area:: 2799.8225; Area:: 2671.221; Area:: 4167.1047; Area:: 5876.6862; Area:: 4337.498; Area:: 15683.417; Area:: 25665.04; Area:: 16332.2982; Area:: 5342.442; Area:: 1498.7523; OKGE: 17972.0532; Area:: 7644.8969 | [22 empty] | OKGE | 26823.96
WFEC | 3.776% | 36415.0292 | 91672.5825 | WFEC | Area:: 3927.7547; Area:: 5723.3197; Area:: 6243.6215; Area:: 624.3621; Area:: 595.6839; Area:: 929.2669; Area:: 1310.5046; Area:: 967.2647; Area:: 3497.4116; Area:: 5723.3197; Area:: 3642.1125; Area:: 1191.3678; Area:: 334.2227; Area:: 1704.8167; WFEC: 91672.5825 | [22 empty] | WFEC | 136824.75
SPS | 13.79% | 132970.6635 | 1180672.7605 | SPS | 14342.3241 |  | 20898.8879 | 307758.3025 | 22798.7868 | 335736.33 | 2279.8787 | 33573.633 | 2175.1592 |  | 3393.2484 |  | 4785.3502 |  | 3531.9986 |  | 12770.9123 |  | 20898.8879 | 307758.3025 | 13299.2923 | 195846.1925 | 4350.3184 |  | 1220.425 |  | 6225.1936 | [23 empty] | SPS | 1762198.15
MIDW | 0.8592% | 8286.1379 | 52012.427 | MIDW | Area:: 893.7496; Area:: 1302.3254; Area:: 1420.7186; Area:: 142.0719; Area:: 135.5462; Area:: 211.4521; Area:: 298.2017; Area:: 220.0984; MIDW: 52012.427; Area:: 795.8262; Area:: 1302.3254; Area:: 828.7525; Area:: 271.0924; Area:: 76.0514; Area:: 387.9263 | [22 empty] | MIDW | 77630.488
SUNF | 1.164% | 11230.9595 | 0 | SUNF | Area:: 1211.3804; Area:: 1765.1605; Area:: 1925.6296; Area:: 192.563; Area:: 183.7182; Area:: 286.6003; Area:: 404.1799; Area:: 298.3194; Area:: 1078.656; Area:: 1765.1605; Area:: 1123.284; Area:: 367.4363; Area:: 103.0795; Area:: 525.7919 | [22 empty] | SUNF
WESTAR | 13.8% | 133059.7318 | 216533.1259 | WESTAR | 14351.9311 |  | 20912.8867 |  | 22814.0582 |  | 2281.4058 |  | 2176.6162 | 32031.5275 | 3395.5213 | 49969.1829 | 4788.5556 | 70469.3605 | 3534.3644 |  | 12779.4667 |  | 20912.8867 |  | 13308.2006 |  | 4353.2324 | 64063.055 | 1221.2425 |  | 6229.3635 | [23 empty] | WESTAR | 323183.77
WEPL | 1.45% | 13983.7275 | 0 | WEPL | Area:: 1508.2962; Area:: 2197.8108; Area:: 2397.6117; Area:: 239.7612; Area:: 228.7485; Area:: 356.8476; Area:: 503.2466; Area:: 371.4391; Area:: 1343.0403; Area:: 2197.8108; Area:: 1398.6068; Area:: 457.4969; Area:: 128.3448; Area:: 654.6663 | [22 empty] | WEPL
MIPU | 4.834% | 46618.9195 | 188065.2356 | MIPU | Area:: 5028.3546; Area:: 7327.0566; Area:: 7993.1526; Area:: 799.3153; Area:: 762.6011; Area:: 1189.6577; Area:: 1677.7224; Area:: 1238.3029; Area:: 4477.4247; MIPU: 188065.2356; Area:: 7327.0566; Area:: 4662.6724; Area:: 1525.2022; Area:: 427.8755; Area:: 2182.525 | [22 empty] | MIPU | 280694.3815
KACP | 9.226% | 88979.2596 | 0 | KACP | Area:: 9597.3754; Area:: 13984.7958; Area:: 15256.1409; Area:: 1525.6141; Area:: 1455.5395; Area:: 2270.6416; Area:: 3202.1869; Area:: 2363.4884; Area:: 8545.8423; Area:: 13984.7958; Area:: 8899.4155; Area:: 2911.079; Area:: 816.6652; Area:: 4165.6792 | [22 empty] | KACP
EMDE | 3.147% | 30350.0328 | 0 | EMDE | Area:: 3273.5793; Area:: 4770.0893; Area:: 5203.7337; Area:: 520.3734; Area:: 496.4716; Area:: 774.4956; Area:: 1092.2374; Area:: 806.1648; Area:: 2914.9107; Area:: 4770.0893; Area:: 3035.5113; Area:: 992.9431; Area:: 278.5572; Area:: 1420.876 | [22 empty] | EMDE
SPRM | 1.851% | 17849.8496 | 0 | SPRM | Area:: 1925.2993; Area:: 2805.4459; Area:: 3060.4865; Area:: 306.0486; Area:: 291.9912; Area:: 455.5063; Area:: 642.3807; Area:: 474.132; Area:: 1714.3546; Area:: 2805.4459; Area:: 1785.2838; Area:: 583.9824; Area:: 163.8286; Area:: 835.6638 | [22 empty] | SPRM
TOTAL | 100% | 964454.1223 | 1848489.4915 | TOTAL | 104026.8075 | 211205.9425 | 151582.4475 | 307758.3025 | 165362.67 | 335736.33 | 16536.267 | 33573.633 | 15776.7225 | 32031.5275 | 24611.6871 | 49969.1829 | 34708.7895 | 70469.3605 | 25618.061 | 52012.427 | 92629.1459 | 188065.2356 | 151582.4475 | 307758.3025 | 96461.5575 | 195846.1925 | 31553.445 | 64063.055 | 8851.9068 | 17972.0532 | 45152.1675 | 91672.5825 | [22 empty] | TOTAL | 2922588.2495
|  | 964454.1223 | 1958134.1272 |  | 104026.8075 | 211205.9425 | 151582.4475 | 307758.3025 | 165362.67 | 335736.33 | 16536.267 | 33573.633 | 15776.7225 | 32031.5275 | 24611.6871 | 49969.1829 | 34708.7895 | 70469.3605 | 25618.061 | 52012.427 | 92629.1459 | 188065.2356 | 151582.4475 | 307758.3025 | 96461.5575 | 195846.1925 | 31553.445 | 64063.055 | 8851.9068 | 17972.0532 | 45152.1675 | 91672.5825 | [23 empty] | 2922588.2495

## MW-mi Allocations
Projects with Mw-mi Impact
2006
[5 empty] | Area: | WERE | Area: | WERE | Area: | OKGE | Area: | OKGE | Area: | OKGE | Area: | MIPU
[5 empty] | Project: | Butler Xfer | Project: | McDowell Conversion and Xfer | Project: | NE Enid - Glenwood | Project: | Razorback - Short Mountain | Project: | Line - Richards Tap - Richards 138 kV | Project: | Nevada - Nevada Plant
[5 empty] | Cost: | 1600000 | Cost: | 7224000 | Cost: | 3732000 | Cost: | 4791277 | Cost: | 1000000 | Cost: | 536000
|  | TOTALS |  |  | FCR: | 0.19123 | FCR: | 0.19123 | FCR: | 0.22353 | FCR: | 0.22353 | FCR: | 0.22353 | FCR: | 0.17483 |  |  |  |  | 100% Zonal E&C (in ATRR)
ZONE | Residential Load Shares | 33% Regional Allocations | 67% MW-mi Allocations | ZONE | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations |  |  |  |  | ZONE | 100% Zonal
CLECO |  |  |  | CLECO | [16 empty] | CLECO | -
SWPA |  |  |  | SWPA | [16 empty] | SWPA | -
AEP | 26.84% | 346343.9111 | 64743.3115 | AEP | 27103.3405 | 0 | 122371.5826 | 0 | 73896.4003 | 0 | 94870.8797 | 64743.3115 | 19800.7503 | 0 | 8300.9577 | 0 |  |  |  |  | AEP
GRDA | 2.336% | 30139.5278 | 0 | GRDA | 2358.586 | 0 | 10649.0156 | 0 | 6430.61 | 0 | 8255.8504 | 0 | 1723.1002 | 0 | 722.3657 | 0 |  |  |  |  | GRDA
OKGE | 16.93% | 218461.3065 | 1037787.6243 | OKGE | 17095.8143 | 0 | 77187.6015 | 15858.8001 | 46611.1966 | 383177.1245 | 59841.1453 | 510506.5486 | 12489.6025 | 128245.151 | 5235.9461 | 0 |  |  |  |  | OKGE | 2128766.6776
WFEC | 3.776% | 48717.0054 | 57320.8216 | WFEC | 3812.3771 | 0 | 17212.8825 | 0 | 10394.3255 | 35798.8627 | 13344.6121 | 0 | 2785.189 | 21521.959 | 1167.6192 | 0 |  |  |  |  | WFEC
SPS | 13.79% | 177891.7296 | 38536.6697 | SPS | 13921.0189 | 0 | 62853.4003 | 14562.7676 | 37955.2174 | 0 | 48728.2852 | 23973.9021 | 10170.2083 | 0 | 4263.5995 | 0 |  |  |  |  | SPS
MIDW | 0.8592% | 11085.4181 | 0 | MIDW | 867.4957 | 0 | 3916.7432 | 0 | 2365.1996 | 0 | 3036.5291 | 0 | 633.762 | 0 | 265.6885 | 0 |  |  |  |  | MIDW
SUNF | 1.164% | 15025.0796 | 21696.2051 | SUNF | 1175.7962 | 0 | 5308.7198 | 21696.2051 | 3205.7711 | 0 | 4115.6852 | 0 | 858.9955 | 0 | 360.1119 | 0 |  |  |  |  | SUNF
WESTAR | 13.8% | 178010.8876 | 1262825.4424 | WESTAR | 13930.3437 | 205001.776 | 62895.5017 | 799516.8517 | 37980.6412 | 139954.8674 | 48760.9251 | 118351.9473 | 10177.0207 | 0 | 4266.4554 | 0 |  |  |  |  | WESTAR | 1687439.992
WEPL | 1.45% | 18707.8067 | 26218.1091 | WEPL | 1463.9901 | 0 | 6609.9153 | 26218.1091 | 3991.5227 | 0 | 5124.4616 | 0 | 1069.5398 | 0 | 448.3772 | 0 |  |  |  |  | WEPL
MIPU | 4.834% | 62368.0443 | 62786.027 | MIPU | 4880.6469 | 0 | 22036.1209 | 0 | 13306.9294 | 0 | 17083.9187 | 0 | 3565.6295 | 0 | 1494.7989 | 62786.027 |  |  |  |  | MIPU | 93710.488
KACP | 9.226% | 119038.8465 | 47730.2849 | KACP | 9315.4529 | 0 | 42059.2699 | 47730.2849 | 25398.2876 | 0 | 32607.243 | 0 | 6805.5433 | 0 | 2853.0498 | 0 |  |  |  |  | KACP
EMDE | 3.147% | 40603.09 | 0 | EMDE | 3177.418 | 0 | 14346.0423 | 0 | 8663.1296 | 0 | 11122.0401 | 0 | 2321.3102 | 0 | 973.1499 | 0 |  |  |  |  | EMDE
SPRM | 1.851% | 23880.0088 | 0 | SPRM | 1868.7437 | 0 | 8437.3779 | 0 | 5095.0706 | 0 | 6541.2365 | 0 | 1365.2386 | 0 | 572.3414 | 0 |  |  |  |  | SPRM
TOTAL | 100% | 1290272.662 | 2619644.4956 | TOTAL | 100971.024 | 205001.776 | 455884.1734 | 925583.0186 | 275294.3015 | 558930.8545 | 353432.8121 | 717575.7095 | 73765.89 | 149767.11 | 30924.461 | 62786.027 |  |  |  |  | TOTAL | 3909917.1576
|  | 1290272.662 | 2619644.4956 |  | 100971.024 | 205001.776 | 455884.1734 | 925583.0186 | 275294.3015 | 558930.8545 | 353432.8121 | 717575.7095 | 73765.89 | 149767.11 | 30924.461 | 62786.027 | [5 empty] | 3909917.1576
2007
[5 empty] | Area: | SPS | Area: | SPS | Area: | EMDE | Area: | OKGE | Area: | AEP | Area: | GRDA | Area: | WERE | Area: | WERE
[5 empty] | Project: | Crosby Co Int Xfer | Project: | Curry Co Int Xfer | Project: | ReinMiller - Tipton Ford | Project: | Richards - Piedmont | Project: | Siloam Springs - Chamber Springs | Project: | Stilwell City Xfer | Project: | HTI Jct - Circleville | Project: | Line - Stranger Creek - Thornton Street 115 kV
[5 empty] | Cost: | 1000000 | Cost: | 1000000 | Cost: | 3215000 | Cost: | 3800000 | Cost: | 6627225 | Cost: | 1800000 | Cost: | 2360000 | Cost: | 2500000
|  | TOTALS |  |  | FCR: | 0.16703 | FCR: | 0.16703 | FCR: | 0.18303 | FCR: | 0.22353 | FCR: | 0.18013 | FCR: | 0.19043 | FCR: | 0.19123 | FCR: | 0.19123 | 100% Zonal E&C (in ATRR)
ZONE | Residential Load Shares | 33% Regional Allocations | 67% MW-mi Allocations | ZONE | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | ZONE | 100% Zonal
CLECO |  |  |  | CLECO | [16 empty] | CLECO | - | bar: Area: to WERE
SWPA |  |  |  | SWPA | [16 empty] | SWPA | - | bar: Area: to WERE
AEP | 26.84% | 375396.5836 | 152226.6468 | AEP | 14795.9305 | 0 | 14795.9305 | 0 | 52125.5171 | 0 | 75242.8513 | 18201.8992 | 105746.2557 | 96904.6962 | 30363.7016 | 19782.5403 | 39977.4273 | 17337.5112 | 42348.9696 | 0 | AEP | 1193781.9209
GRDA | 2.336% | 32667.7484 | 536306.1363 | GRDA | 1287.5709 | 0 | 1287.5709 | 0 | 4536.0649 | 0 | 6547.7808 | 0 | 9202.247 | 364734.5764 | 2642.309 | 171571.5599 | 3478.9143 | 0 | 3685.2906 | 0 | GRDA | 342779.4
OKGE | 16.93% | 236786.6894 | 726315.2197 | OKGE | 9332.7418 | 0 | 9332.7418 | 0 | 32878.9051 | 0 | 47460.4896 | 506392.4574 | 66700.9421 | 168545.2038 | 19152.333 | 38308.0978 | 25216.3261 | 13069.4607 | 26712.2098 | 0 | OKGE | 849425.4
WFEC | 3.776% | 52803.577 | 19202.0484 | WFEC | 2081.2072 | 0 | 2081.2072 | 0 | 7332.016 | 0 | 10583.7183 | 19202.0484 | 14874.351 | 0 | 4270.982 | 0 | 5623.2562 | 0 | 5956.8392 | 0 | WFEC
SPS | 13.79% | 192813.9789 | 292934.9582 | SPS | 7599.5956 | 111912.11 | 7599.5956 | 111912.11 | 26773.0949 | 0 | 38646.7916 | 25318.613 | 54314.1765 | 20106.0318 | 15595.6298 | 0 | 20533.5029 | 23686.0934 | 21751.592 | 0 | SPS | 334066
MIDW | 0.8592% | 12015.306 | 0 | MIDW | 473.5729 | 0 | 473.5729 | 0 | 1668.3797 | 0 | 2408.2955 | 0 | 3384.6169 | 0 | 971.85 | 0 | 1279.5562 | 0 | 1355.4621 | 0 | MIDW
SUNF | 1.164% | 16285.4417 | 0 | SUNF | 641.8765 | 0 | 641.8765 | 0 | 2261.3074 | 0 | 3264.1828 | 0 | 4587.4804 | 0 | 1317.2371 | 0 | 1734.2994 | 0 | 1837.1815 | 0 | SUNF
WESTAR | 13.8% | 192943.1323 | 484460.0024 | WESTAR | 7604.6861 | 0 | 7604.6861 | 0 | 26791.0284 | 0 | 38672.6786 | 0 | 54350.558 | 39257.5942 | 15606.0762 | 0 | 20547.2569 | 167915.6388 | 21766.162 | 277286.7693 | WESTAR | 929392.38
WEPL | 1.45% | 20277.0902 | 65045.1916 | WEPL | 799.2039 | 0 | 799.2039 | 0 | 2815.5659 | 0 | 4064.2514 | 0 | 5711.8963 | 0 | 1640.0989 | 0 | 2159.3854 | 65045.1916 | 2287.4845 | 0 | WEPL
MIPU | 4.834% | 67599.7181 | 0 | MIPU | 2664.3842 | 0 | 2664.3842 | 0 | 9386.5273 | 0 | 13549.3922 | 0 | 19042.3072 | 0 | 5467.758 | 0 | 7198.9542 | 0 | 7626.0108 | 0 | MIPU
KACP | 9.226% | 129024.2873 | 58352.2295 | KACP | 5085.3803 | 0 | 5085.3803 | 0 | 17915.6071 | 0 | 25861.0645 | 0 | 36345.1237 | 0 | 10436.0432 | 0 | 13740.293 | 15323.7239 | 14555.3952 | 43028.5057 | KACP
EMDE | 3.147% | 44009.0349 | 478980.6511 | EMDE | 1734.5779 | 0 | 1734.5779 | 0 | 6110.854 | 394262.2337 | 8820.9787 | 0 | 12396.9979 | 84718.4174 | 3559.6414 | 0 | 4686.6915 | 0 | 4964.7156 | 0 | EMDE | 588451.095
SPRM | 1.851% | 25883.1567 | 25567.3672 | SPRM | 1020.1622 | 0 | 1020.1622 | 0 | 3593.9936 | 0 | 5187.9069 | 0 | 7291.081 | 25567.3672 | 2093.5418 | 0 | 2756.397 | 0 | 2919.9121 | 0 | SPRM
TOTAL | 100% | 1398505.7447 | 2839390.4513 | TOTAL | 55120.89 | 111912.11 | 55120.89 | 111912.11 | 194188.8613 | 394262.2337 | 280310.382 | 569115.018 | 393948.0339 | 799833.887 | 113117.202 | 229662.198 | 148932.2604 | 302377.6196 | 157767.225 | 320315.275 | TOTAL | 4237896.1959
|  | 1398505.7447 | 2839390.4513 |  | 55120.89 | 111912.11 | 55120.89 | 111912.11 | 194188.8613 | 394262.2337 | 280310.382 | 569115.018 | 393948.0339 | 799833.887 | 113117.202 | 229662.198 | 148932.2604 | 302377.6196 | 157767.225 | 320315.275 |  | 4237896.1959
2008
[5 empty] | Area: | OKGE | Area: | WERE | Area: | WFEC | Area: | EMDE | Area: | AEPW
[5 empty] | Project: | Etowah - Tribbey | Project: | Hutchinson 115 kV Voltage Conv | Project: | Sayre - Moorewood - Voltage Conv | Project: | Riverdale - Ozarks | Project: | Fayetteville 69 kV Conv
[5 empty] | Cost: | 1900000 | Cost: | 1900000 | Cost: | 12000000 | Cost: | 14057000 | Cost: | 21000000
|  | TOTALS |  |  | FCR: | 0.22353 | FCR: | 0.19123 | FCR: | 0.18243 | FCR: | 0.18303 | FCR: | 0.18013 | [6 empty] | 100% Zonal E&C (in ATRR)
ZONE | Residential Load Shares | 33% Regional Allocations | 67% MW-mi Allocations | ZONE | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | 33% Regional Allocations | 67% MW-mi Allocations | [6 empty] | ZONE | 100% Zonal
CLECO |  |  |  | CLECO | [16 empty] | CLECO | -
SWPA |  |  |  | SWPA | [16 empty] | SWPA | -
AEP | 26.84% | 826719.9949 | 876142.5724 | AEP | 37621.4256 | 0 | 32185.2169 | 0 | 193920.913 | 61575.9976 | 227909.2983 | 31090.8116 | 335083.1411 | 783475.7632 | [6 empty] | AEP | 3782793
GRDA | 2.336% | 71942.7986 | 208404.2475 | GRDA | 3273.8904 | 0 | 2800.8208 | 0 | 16875.3789 | 0 | 19833.115 | 0 | 29159.5934 | 208404.2475 | [6 empty] | GRDA
OKGE | 16.93% | 521465.2961 | 1594889.5328 | OKGE | 23730.2448 | 284557.509 | 20301.2795 | 0 | 122318.3507 | 385189.3825 | 143757.0042 | 0 | 211358.417 | 925142.6413 | [6 empty] | OKGE | 424712.7
WFEC | 3.776% | 116287.081 | 1018588.8107 | WFEC | 5291.8592 | 0 | 4527.1978 | 0 | 27277.0673 | 872715.3728 | 32057.9001 | 0 | 47133.0567 | 145873.4379 | [6 empty] | WFEC | 2189196
SPS | 13.79% | 424626.0584 | 110123.6382 | SPS | 19323.3958 | 0 | 16531.2099 | 0 | 99603.0983 | 68215.3775 | 117060.465 | 0 | 172107.8894 | 41908.2607 | [6 empty] | SPS
MIDW | 0.8592% | 26460.7995 | 0 | MIDW | 1204.1477 | 0 | 1030.1512 | 0 | 6206.8202 | 0 | 7294.6854 | 0 | 10724.995 | 0 | [6 empty] | MIDW
SUNF | 1.164% | 35864.7384 | 0 | SUNF | 1632.0914 | 0 | 1396.258 | 0 | 8412.6704 | 0 | 9887.1533 | 0 | 14536.5653 | 0 | [6 empty] | SUNF
WESTAR | 13.8% | 424910.4875 | 497133.7522 | WESTAR | 19336.3393 | 0 | 16542.2831 | 243439.609 | 99669.8159 | 79065.1896 | 117138.8761 | 31109.1728 | 172223.1732 | 143519.7808 | [6 empty] | WESTAR | 363342.7
WEPL | 1.45% | 44655.3768 | 37906.1418 | WEPL | 2032.1257 | 0 | 1738.4882 | 0 | 10474.6607 | 0 | 12310.5473 | 0 | 18099.5549 | 37906.1418 | [6 empty] | WEPL
MIPU | 4.834% | 148871.9957 | 72521.8102 | MIPU | 6774.6961 | 0 | 5795.7682 | 0 | 34920.4005 | 0 | 41040.8751 | 41541.3194 | 60340.2558 | 30980.4908 | [6 empty] | MIPU
KACP | 9.226% | 284144.7226 | 149406.0746 | KACP | 12930.5322 | 0 | 11062.1003 | 0 | 66650.8665 | 0 | 78332.7182 | 52444.4003 | 115168.5054 | 96961.6744 | [6 empty] | KACP
EMDE | 3.147% | 96919.2335 | 1458505.784 | EMDE | 4410.4894 | 0 | 3773.1839 | 0 | 22734.0168 | 0 | 26718.5923 | 1399652.0626 | 39282.9512 | 58853.7214 | [6 empty] | EMDE | 2572894.881
SPRM | 1.851% | 57001.3797 | 229446.954 | SPRM | 2593.9534 | 0 | 2219.1332 | 0 | 13370.6208 | 0 | 15714.0804 | 168001.8037 | 23103.5919 | 61445.1503 | [6 empty] | SPRM
TOTAL | 100% | 3079869.9627 | 6253069.3183 | TOTAL | 140155.191 | 284557.509 | 119903.091 | 243439.609 | 722434.68 | 1466761.32 | 849055.3107 | 1723839.5703 | 1248321.69 | 2534471.31 | [6 empty] | TOTAL | 9332939.281
|  | 3079869.9627 | 6253069.3183 |  | 140155.191 | 284557.509 | 119903.091 | 243439.609 | 722434.68 | 1466761.32 | 849055.3107 | 1723839.5703 | 1248321.69 | 2534471.31 | [7 empty] | 9332939.281

## MW-mi Impacts
2006
| Butler Xfer |  |  | McDowell Conversion and Xfer |  |  | NE Enid - Glenwood |  |  | Razorback - Short Mountain |  |  | Richards Tap - Richards |  |  | Nevada - Nevada Plant
| Net of Positive |  |  | Net of Positive |  |  | Net of Positive |  |  | Net of Positive |  |  | Net of Positive |  |  | Net of Positive
ZONE | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min
CLECO | 0 | 0 | 0% | 0 | 0 | 0% | 15.36 | 2.9633 | 3.118% | 15.36 | 2.3521 | 2.498% | 6.01 | 0 | 0% | 0 | 0 | 0%
SWPA | 2.35 | 0 | 0% | 0.6976 | 0 | 0% | 14.4576 | 2.7892 | 2.935% | 66.6976 | 10.2135 | 10.85% | 24.3776 | 4.2552 | 0% | 0.2 | 0 | 0%
AEP | 22.3377 | 2.0967 | 0% | 21.0083 | 0.47395 | 0% | 6.2098 | 0 | 0% | 48.0645 | 7.3602 | 7.818% | 43.919 | 7.6663 | 0% | 0 | 0 | 0%
GRDA | 6.86 | 0 | 0% | 4.2827 | 0 | 0% | 9.14 | 0 | 0% | 13.52 | 2.0703 | 0% | 19.0627 | 3.3275 | 0% | 0 | 0 | 0%
OKGE | 55.9396 | 5.2506 | 0% | 74.1964 | 1.6739 | 1.713% | 317.2551 | 61.2065 | 64.41% | 378.9927 | 58.0356 | 61.65% | 392.1489 | 68.4514 | 85.63% | 0.2 | 0 | 0%
WFEC | 8.95 | 0 | 0% | 12.28 | 0.27704 | 0% | 29.64 | 5.7183 | 6.017% | 9.9 | 0 | 0% | 65.81 | 11.4874 | 14.37% | 0.02 | 0 | 0%
SPS | 5.34 | 0 | 0% | 68.1328 | 1.5371 | 1.573% | 12.37 | 2.3865 | 0% | 17.7979 | 2.7254 | 2.895% | 1.5 | 0 | 0% | 0.41 | 0 | 0%
MIDW | 4.7639 | 0 | 0% | 33.3788 | 0.75303 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0%
SUNF | 12.2734 | 1.152 | 0% | 101.507 | 2.29 | 2.344% | 5.6634 | 0 | 0% | 11.3634 | 1.7401 | 0% | 2.73 | 0 | 0% | 0 | 0 | 0%
WESTAR | 974.8435 | 91.5007 | 100% | 3740.5877 | 84.3882 | 86.38% | 115.8769 | 22.3556 | 23.52% | 87.8628 | 13.4545 | 14.29% | 8.368 | 0 | 0% | 0.56 | 0 | 0%
WEPL | 8.15 | 0 | 0% | 122.663 | 2.7673 | 2.833% | 3.42 | 0 | 0% | 4.6 | 0 | 0% | 1.7066 | 0 | 0% | 0 | 0 | 0%
MIPU | 2.7405 | 0 | 0% | 35.535 | 0.80167 | 0% | 4.73 | 0 | 0% | 4.73 | 0 | 0% | 5.3121 | 0 | 0% | 2.09 | 0 | 100%
KACP | 9.1895 | 0 | 0% | 223.309 | 5.0379 | 5.157% | 13.3759 | 2.5805 | 0% | 13.3759 | 2.0483 | 0% | 27.568 | 4.8121 | 0% | 0 | 0 | 0%
EMDE | 3.43 | 0 | 0% | 1.36 | 0 | 0% | 2.66 | 0 | 0% | 1.51 | 0 | 0% | 2.96 | 0 | 0% | 0 | 0 | 0%
SPRM | 0 | 0 | 0% | 0.39 | 0 | 0% | 0.27 | 0 | 0% | 0.07 | 0 | 0% | 0.39 | 0 | 0% | 0 | 0 | 0%
TOTAL | 1065.3942 | 100 | 100% | 4432.5979 | 100 | 100% | 518.3355 | 100 | 100% | 653.0347 | 100 | 100% | 572.8863 | 100 | 100% | 0 | 0 | 100%
2007
| Crosby Co Int Xfer |  |  | Curry Co Int Xfer |  |  | ReinMiller - Tipton Ford |  |  | Richards - Piedmont |  |  | Siloam Springs - Chamber Springs |  |  | Stilwell City Xfer |  |  | HTI Jct - Circleville |  |  | Stranger Creek - Thorton
| Net of Positive |  |  | Net of Positive |  |  | Net of Positive |  |  | Net of Positive |  |  | Net of Positive |  |  | Net of Positive |  |  | Net of Positive |  |  | Net of Positive
ZONE | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % base allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min
CLECO | 0 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 1.51 | 0 | 0% | 5.4 | 0 | 0% | 8.32 | 0 | 0% | 5.85 | 0 | 0% | 12.4954 | 0.2092 | 0%
SWPA | 2.23 | 0 | 0% | 2.23 | 0 | 0% | 5.73 | 0 | 0% | 12.58 | 0.98906 | 0% | 167.2828 | 11.2112 | 11.37% | 442.4184 | 14.9403 | 16.27% | 2.23 | 0 | 0% | 9.15 | 0 | 0%
AEP | 8.8281 | 0 | 0% | 8.8281 | 0 | 0% | 0.6173 | 0 | 0% | 39.2152 | 3.0832 | 3.198% | 158.0374 | 10.5916 | 10.74% | 196.068 | 6.6212 | 7.212% | 15.629 | 5.7337 | 5.734% | 25.4558 | 0.42619 | 0%
GRDA | 0.2 | 0 | 0% | 0.2 | 0 | 0% | 5.2327 | 0 | 0% | 6.97 | 0 | 0% | 594.8288 | 39.8653 | 40.42% | 1700.4736 | 57.4245 | 62.55% | 3.7332 | 0 | 0% | 8.5032 | 0 | 0%
OKGE | 0.65 | 0 | 0% | 0.65 | 0 | 0% | 0 | 0 | 0% | 1091.0011 | 85.7764 | 88.98% | 274.8726 | 18.4219 | 18.68% | 379.6778 | 12.8216 | 13.97% | 11.7815 | 4.3222 | 4.322% | 69.0242 | 1.1556 | 0%
WFEC | 1.1 | 0 | 0% | 1.1 | 0 | 0% | 0 | 0 | 0% | 41.37 | 3.2526 | 3.374% | 9.3 | 0 | 0% | 16.08 | 0.54302 | 0% | 1.1 | 0 | 0% | 10.55 | 0.17663 | 0%
SPS | 34.7119 | 100 | 100% | 42.6119 | 100 | 100% | 0 | 0 | 0% | 54.5479 | 4.2886 | 4.449% | 32.79 | 2.1976 | 2.228% | 35.77 | 1.2079 | 0% | 21.3519 | 7.8333 | 7.833% | 0.2 | 0 | 0%
MIDW | 0 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 7.8244 | 0 | 0% | 2.75 | 0 | 0% | 0 | 0 | 0% | 0.47 | 0 | 0% | 8.06 | 0 | 0%
SUNF | 0 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 10.9734 | 0.86275 | 0% | 10.3034 | 0.69053 | 0% | 5.7 | 0 | 0% | 0.45 | 0 | 0% | 86.927 | 1.4554 | 0%
WESTAR | 0.39 | 0 | 0% | 0.49 | 0 | 0% | 9.34 | 0 | 0% | 22.2256 | 1.7474 | 0% | 64.0234 | 4.2908 | 4.35% | 77.4309 | 2.6148 | 0% | 151.3683 | 55.5318 | 55.53% | 4856.126 | 81.3035 | 86.57%
WEPL | 0 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 2.34 | 0 | 0% | 4.38 | 0 | 0% | 22.2 | 0.74969 | 0% | 58.6353 | 21.5112 | 21.51% | 49.46 | 0.82808 | 0%
MIPU | 0 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0% | 5.61 | 0 | 0% | 13.2706 | 0.44815 | 0% | 4.896 | 0 | 0% | 109.2431 | 1.829 | 0%
KACP | 0 | 0 | 0% | 0.11 | 0 | 0% | 3.08 | 0 | 0% | 3.08 | 0 | 0% | 10.1 | 0.6769 | 0% | 32.2028 | 1.0875 | 0% | 13.8136 | 5.0677 | 5.068% | 753.5587 | 12.6164 | 13.43%
EMDE | 0 | 0 | 0% | 0 | 0 | 0% | 34.49 | 100 | 100% | 0 | 0 | 0% | 138.1634 | 9.2597 | 9.388% | 31.723 | 1.0713 | 0% | 0 | 0 | 0% | 4.05 | 0 | 0%
SPRM | 0 | 0 | 0% | 0 | 0 | 0% | 2.96 | 0 | 0% | 0 | 0 | 0% | 41.6966 | 2.7945 | 2.833% | 13.92 | 0.47007 | 0% | 0 | 0 | 0% | 0.54 | 0 | 0%
TOTAL | 34.7119 | 100 | 100% | 42.6119 | 100 | 100% | 34.49 | 100 | 100% | 1271.9132 | 100 | 100% | 1492.0984 | 100 | 100% | 2961.235 | 100 | 100% | 272.5796 | 100 | 100% | 5972.8403 | 100 | 100%
2008
| Etowah - Tribbey |  |  | Hutchinson 115 kV Voltage Conv |  |  | Sayre - Moorewood - Voltage Conv |  |  | Riverdale - Ozarks |  |  | Fayetteville 69 kV Conv
| Net of Positive |  |  | Net of Positive |  |  | Net of Positive |  |  | Net of Positive |  |  | Net of Positive
ZONE | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min | MWMI Impact | % allocation | % 100k Min
CLECO | 7.19 | 0 | 0% | 1.35 | 0 | 0% | 93.53 | 0.52775 | 0% | 5.85 | 0 | 0% | 74.61 | 5.576 | 5.576%
SWPA | 28.72 | 3.5902 | 0% | 2.23 | 0 | 0% | 37.8192 | 0.2134 | 0% | 31.3568 | 3.1293 | 3.129% | 77.9968 | 5.8291 | 5.829%
AEP | 24.4881 | 3.0611 | 0% | 16.2109 | 1.9056 | 0% | 722.0542 | 4.0742 | 4.198% | 17.5069 | 1.7471 | 1.747% | 366.4584 | 27.3872 | 27.39%
GRDA | 14.55 | 1.8188 | 0% | 0.2 | 0 | 0% | 102.0792 | 0.57599 | 0% | 8.0732 | 0 | 0% | 97.4778 | 7.285 | 7.285%
OKGE | 638.0079 | 79.7544 | 100% | 1.4772 | 0 | 0% | 4516.8188 | 25.4863 | 26.26% | 9.9727 | 0 | 0% | 432.7209 | 32.3393 | 32.34%
WFEC | 18.91 | 2.3639 | 0% | 15.24 | 1.7915 | 0% | 10233.66 | 57.7439 | 59.5% | 1.1 | 0 | 0% | 68.23 | 5.0992 | 5.099%
SPS | 27.5 | 3.4376 | 0% | 24.3619 | 2.8638 | 0% | 799.9091 | 4.5135 | 4.651% | 1.91 | 0 | 0% | 19.6019 | 1.4649 | 1.465%
MIDW | 0 | 0 | 0% | 0.1 | 0 | 0% | 0.55 | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0%
SUNF | 0 | 0 | 0% | 43.1768 | 5.0754 | 0% | 85.7104 | 0.48362 | 0% | 1.2 | 0 | 0% | 4.11 | 0 | 0%
WESTAR | 27.93 | 3.4914 | 0% | 715.81 | 84.1437 | 100% | 927.1365 | 5.2314 | 5.39% | 17.5172 | 1.7482 | 1.748% | 67.1291 | 5.0169 | 5.017%
WEPL | 19.86 | 2.4826 | 0% | 35.9 | 4.2201 | 0% | 20.07 | 0.11325 | 0% | 0.1 | 0 | 0% | 17.73 | 1.325 | 1.325%
MIPU | 0 | 0 | 0% | 2.11 | 0 | 0% | 36.5002 | 0.20595 | 0% | 23.3915 | 2.3344 | 2.334% | 14.4906 | 1.083 | 1.083%
KACP | 6.1003 | 0 | 0% | 0.42 | 0 | 0% | 147.2157 | 0.83067 | 0% | 29.5309 | 2.9471 | 2.947% | 45.3523 | 3.3894 | 3.389%
EMDE | 2.94 | 0 | 0% | 0 | 0 | 0% | 7.379 | 0 | 0% | 788.129 | 78.6531 | 78.65% | 27.5279 | 2.0573 | 2.057%
SPRM | 2.96 | 0 | 0% | 0 | 0 | 0% | 3.29 | 0 | 0% | 94.6 | 9.4408 | 9.441% | 28.74 | 2.1479 | 2.148%
TOTAL | 799.966 | 100 | 100% | 850.6996 | 100 | 100% | 17722.5033 | 100 | 100% | 1002.0322 | 100 | 100% | 1338.0658 | 100 | 100%

## 2007 Q1 Project List
| 2007, First Quarter: Potential Base Plan Upgrades | [7 empty] | Project Completed | Engineering Completed | Obtained ROW | In Construction | Done Energized
The following are transmission reliability improvements that meet criteria for designation as Base Plan Upgrades
in accordance with the proposed Base Plan Guidelines Task Force report and the SPP Open Access Transmission Tariff.
Potential Base Plan Upgrade identified in the SPP RTO Transmission Expansion Planning Process
Mw-mi | Area | Project Name | In-Service Date | 2006 Expansion Plan Date | Cost Estimate | Base Plan Reason | Project Description/Comments | Project Justification
- | AEPW | Line - Lone Star South - Pittsburg 138 kV | 2006-06-01 | - | 50000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 6/1/2006 TPL002 | Replace CT | Lone Star South-Pittsburg 138 kV over load for an outage of Petty-Chapel Hill Rec 138 | Y | Y | N | N | N
- | AEPW | Line - Elk City - Elk City 69 kV | 06/1/07 * | 2007-06-01 | 100000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Replace CTS & jumpers. Limits on AEP end will be 600A switches and Breaker | To address overloads @ Elk City 69 - Elk City for the MOREWOOD - MORWOOD 69 kv outage | N | N | N | N | N
- | AEPW | Line - Porter Hill - Elgin Junction | 06/1/07 * | 2007-06-01 | 200000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Replace Switches & reset CT @ Elgin Jct. Replace switches @ Porter Hill. $200,000 12 month lead time | To address overload @Porter Hill - Elgin Junction 1 for Lawton Eastside - Lawton Gore North outage | N | N | N | N | N
- | AEPW | Device - Broken Arrow Water | 06/1/07 * | 2007-06-01 | 550000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install 6 MVA Cap at Broken Arrow water 6 MVAR | To address low voltages @Broken Arrow Water & Coweta for an outage of Tulsa SE transformer | N | N | N | N | N
- | AEPW | Device - Hobart | 06/1/07 * | 2007-06-01 | 550000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install 4.8 MVAR cap at Hobart 54128 | To address low voltage @Hobart for the Hobart - Hobart Junction 69kV outage | N | N | N | N | N
- | AEPW | Line - Northwest Texarkana - Alumax Tap | 2008-06-01 | 2007-06-01 | 1750000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Rebuild 2 miles of 1590 ACAR with 2156 ACSR, Replace wavetrap & jumpers with 2156 ACSR. Replace Switch 2285 @ Alumax Tap. | To addres overload @Northwest Texarkana - Alumax Tap 1 for SPP-AEPW-29 outage | N | N | N | N | N
- | AEPW | Line - Bann - Kings Highway 69 kV | 2008-06-01 | - | 50000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 6/1/2008 TPL002 | Replace Switch in King Hwy substation | Bann-Kings Highway 69 kV for loads for outage Bann-SE Texarkana 138 kV line | Y | Y | N | N | N
Y | AEPW | Multi - Fayetteville 69 kV conversion | 2008-06-01 | 2008-06-01 | 21000000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2008 TPL002 | Convert 69 KV line to 161 kV | Dyess-S Springdale 161kv overloads conductor for outage of Chamber Springs-Farmington 161 kV | N | N | N | N | N
Y | EMDE | Multi - Riverdale - Ozarks 161 kV Ckt 1 | 2008-06-01 | 2010-06-01 | 14057000 | Identified in the2006 SPP Expansion Plan as needed in 6/1/2010 TPL002 | Build 161 kV line from AECI's Riverdale substation to a new substation at Ozark. Install a 100 MVA 161/69 Auto-xfmr in the Ozark substation. Split the 69 kV line from Forsyth to Ozark #434 at this new substation. | Low voltage at the Ozark #330 substation during the outage of Blackhawk #415 to Ozark #330. Also, under normal conditions EDE exceeds their contract limit on the Blackhawk to Jamevilles interconnection with AECI. | N | N | N | N | N
- | EMDE | Line - Sub 167 - Riverton - Sub 406 - Riverton S | 06/1/08 * | 2008-06-01 | 20000 | Identified in the2006 SPP Expansion Plan as needed in 6/1/2008 TPL002 | Change Relay Settings and change jumpers on switch at Riverton Sub #406 | To address overload @SUB 167 - RIVERTON - SUB 406 - RIVERTON SOUTH 1 for outage of HOCKERVILLE 161/69 Xfr | N | N | N | N
- | MIDW | Multi - Knoll - Hays - Vine 115 kV | 2009-06-30 | 2008-06-01 | 536000 | Identified in the 2006 SPP Expansion Plan as needed in 2008 TPL002 | Tap Vine - Knoll 115 kV and reconductor Hays Plant - Vine Street and S. Hays - Hays Plant | To address overload of Vine - Hays Plant overload for the Knoll 230/115 kV Transformer outage
- | MIPU | Line - Lake Road to Industrial Park 161 kV | 2009-06-01 | 2007-06-01 | 250000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Replace existing structures to allow for higher rating | To address overload of Lake Road to Industrial Park 161 kV for outage of St. Joseph to Woodbine 161 kV
- | MIPU | Line - Blue Springs - Duncan Road 161 kV | 2010-06-01 | 2008-06-01 | 1605500 | Itentified by Tarrif Studies group as an Expansion Plan project needed 6/1/2008 | Upgrade to conductor Bundled Drake | Identified as Expansion Plan project by the Tarrif Studies group in AGS 2006-1 Blue Sprins East to Duncan 161 kV line over loads for an outage of PLEASANT HILL () 345/161/13.8KV TRANSFORMER CKT 1 over load in years 2006 throough 2010
- | OKGE | Line - Brown Explorer Tap 138kV | 2006-06-01 |  | 25031.22 | TO Study - NERC TPL-002 | Upgrade CT's at Brown Substation | The 2010 Summer Peak Contingency Analysis indicates that the loss of the Bus # 55120 RUSSET 138kV to Bus # 55147 GLASSES4 138 line causes and overload on the Bus # 52802 S BROWN 138kV to 55157 BROWN 138kV section. To mitigate an (N-1) condition as determined by SPP Planning standards and NERC TPL-002-0. OGE operations also seen very low voltage during summer 2005 due to the WFEC Hugo plant trip off.
Y | OKGE | Line - NE Enid - Glenwood 138 kV | 2006-12-31 | - | 3732000 | Project to meet OG&E Operating Practice S3-5 | Part of a long term project per K Study 5140.3 to enhance the transmission system in Enid, OK. This is the last phase of the project. | Project to meet OG&E Operating Practice S3-5, which is part of OG&E Planning Criteria, which qualifies this project for Regional Cost Allocation and inclusion in the Plant. [Due to OGE K5140.3 study in 2001 that identified violations of OGE S3-5 operatin | N | Y | Y | Y | N
Y | OKGE | Line - Razorback - Short Mountain 69 kV | 2006-12-31 | - | 4791277 | Project to meet OGE's operating guides S3-5. | New 69(161)kV transmission line from Razorback to Short Mountain | As a result of OGE internal K study 10086 for future conversion. Supporting Study has been submitted to SPP in the past. Project was initiated to close the radial transmission lines at Short Mountain and Razorback Substation per OGE's operating guides S3 | N | Y | Y | Y | N
Y | OKGE | Line - Etowah - Tribbey 69 kV | 2008-06-01 | - | 1900000 | TO Study - NERC TPL-002 | Close NO switch of Etowah-Tribbey by rebuilding Etowah and installing 69kV breakers. NOTE: Overloads Midwest - Franklin so it must take place after the Midwest - Franklin project is complete | Low voltage around Spring Hill, Little Axe, Etowah, Macomoc for OKGEMTL-24. Violates NERC TPL-002-0 and SPP Criteria 3.4. | N | N | N | N | N
- | OKGE | Line - Westmoore - Pennsylvania 138 kV | 2009-06-01 | 2007-10-01 | 250000 | Identified in the 2006 SPP Expansion Plan as needed in 10/1/2007 TPL002 | Replace the disconnect switches for breaker 108 at Pennsylvania Substation. Replace the 1200A trap. Increase CTR. Relay replacement may be required. | Identifid By the AG study as an Expansion Plan Project being need in 2007 fall for an outage CZECH HALL -CIMARRON 138 or an outage of CZECH HALL - INDIAN HILLS 138
- | SWPS | XFR - Carlsbad Int 115 kV - Carlsbad Int 69 kV | 06/1/07 * | 2007-06-01 | 2750000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Upgrade 115/69 kV transformer. | To address overload @Carlsbad 115/69 kV transformer 1 & 2 for outage | N | N | N | N
Y | SWPS | XFR - Crosby Co Int 69 kV - Crosby Co Int 115 kV | 06/1/07 * | 2007-06-01 | 1000000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Add third transformer from spare stock | To address overload @Crosby 115/69 kV transformer 1 & 2 for outage of the other Crosby transformer | N | N | N | N
Y | SWPS | XFR - Curry Co Int 69 kV - Curry Co Int 115 kV | 06/1/07 * | 2007-06-01 | 1000000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Add third transformer from spare stock | To address overload @Curry 115/69 kV transformer 1&2 for outage
- | SWPS | XFR - Gaines Co Int 69 kV - Gaines Co Int 115 kV | 06/1/07 * | 2007-06-01 | 2750000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Replace both gaines transformers with 84 MVA xf | To address overload @Northwest - Gaines 115/69 kV transformer 1 & 2 for outage of one of Graines XF overloads the other | N | N | N | N
- | SWPS | Device - San Andress Sub | 06/1/07 * | 2007-06-01 | 750000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install 1 - 14.4 Mvar cap bank on the 115 kV bus at San Andress | Voltage below critera at San Andress bus for outage os San Andress toDenver City Interchange S | N | N | N | N | N
- | SWPS | XFR - Lubbock East 115/69 kV | 2008-06-01 | 2007-06-01 | 2750000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Upgrade both existing transformer | To address loss of parallel transformer | N | N | N | N | N
- | SWPS | XFR - Mustang Sta N. 115 kV - Mustang Sta 230 kV | 06/1/08 * | 2008-06-01 | 3000000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2008TPL002 | Upgrade Transformer 230/115 kV 252/289 MVA | To address overload @Mustang 230/115 kV transformer 1 for outage | N | N | N | N
- | SWPS | Device - Bowers | 06/1/08 * | 2008-06-01 | 300000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2008TPL002 | INSTALL 14.4 MVAR CAP BOWERS 69 KV | Voltage below criteria at the Canadian bus for outage of Bowers to Grapevine 115kV
- | SWPS | XFR - Cochran 115/69 kV | 2009-09-01 | 2008-06-01 | 2750000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2008 TPL002 | Upgrade both existing transformer | To address loss of parallel transformer
- | SWPS | XFR - Artesia 115/69 kV | 2010-12-01 | 2007-06-01 | 2750000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Upgrade both existing transformer | To address loss of parallel transformer
- | SWPS | XFR - NE Hereford 115/69 kV | 2010-06-01 | 2008-06-01 | 1750000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2008 TPL002 | Add second 115/69 kV transformer | NE Herford 115/69 kV XF overload for outage of Herferd to Deaf Smith County Interchange 115 kV this also relives the overload of the Hereford Interchange 115/69 kV XF for the outage of NE Herford 115/69 kV XF
- | WEPL | GREENSBURG - JUDSON LARGE 115KV CKT 1 | 06/1/07 * | 2007-06-01 | 148000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Replace relays (upgrade protection system) | To address overload of the GREENSBURG - JUDSON LARGE 115KV line for the outage of the Mullergren-Spearville 230 KV | N | N | N | N | N
- | WERE | Line - Cities Service - 3rd & VanBuren 69 kV | 2006-03-01 | - | 1700000 | TO Study Identified as Needed June 2006 | Tear down / Rebuild 3.18-mile line using 795 kcmil ACSR; Project is part of a long range plan to correct service issues in the City of Hutchinson area. | Addresses overloads for loss of Circle-Davis 115 kV line, NERC Reliability Standard TPL-002-0. Transmission Operating Directive 1205 no longer effective. | Y
- | WERE | Line - Golden Plain - Gatz 69 kV Rebuild | 06/1/07 * | 2007-06-01 | 590000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Rebuild Gatz - Golden Plain Tap 69 kV line. | To address line overload issues for the loss of Halstead (57736) - Mud Creek (57744) 69 kV line. | N | N | N | N | N
- | WERE | Line - Hesston - Golden Plain 69 kV Rebuild | 06/1/07 * | 2007-06-01 | 1250000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Rebuild Hesston - Golden Plain Tap 69 kV line. | To address line overload issues for the loss of Halstead (57736) - Mud Creek (57744) 69 kV line. | N | N | N | N | N
Y | WERE | Line - HTI Junction - Circleville 115 kV | 06/1/07 * | 2007-06-01 | 2360000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Rebuild 115 kV line | See Westar Five-Year Transmission Construction Recommendations, August 12,2005, P. 11 | N | N | N | N | N
- | WERE | Line - Murry Gill Energy Center - MacArthur 69 kV | 2007-07-01 | 2008-06-01 | 143000 | Identified in the2006 SPP Expansion Plan as needed in 6/1/2008 TPL002 | Replace bus, jumpers and disconnect switches at MacArthur 69 kV substation to increase line capacity to conductor rating | To address line overload issues for the loss of Gill Energy Center East (57795) - Gill Energy Center Jcn (57798) 69 kV line. | N | N | N | N | N
- | WERE | Line - Coffeyville - CRA 69 kV Rebuild | 06/1/08 * | 2008-06-01 | 250000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2008 TPL002 | Rebuild Coffeyville - CRA 69 kV line. | To address line overload issues for the loss of CRA (57685) - Liberty (57697) 69 kV line.
- | WERE | Line - Dearing - Coffeyville 69 kV Rebuild | 06/1/08 * | 2008-06-01 | 390000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2008 TPL002 | Rebuild Dearing - Coffeyville 69 kV line. | To address line overload issues for the loss of CRA (57685) - Liberty (57697) 69 kV line. | N | N | N | N | N
- | WERE | Device - Sunset 69 kV Cap | 2008-06-30 | 2007-06-01 | 550000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install 10 Mvar cap at Sunset 69 kV (bus # 57844) | Voltage support needed due to low voltage from loss of SWPS #1 and loss of Brookline-to-Morgan 345 kV line. | N | N | N | N | N
Y | WERE | Multi - Hutchinson 115 kV conversion | 2008-12-31 | - | 1900000 | TO study identified as needed June 2006. Project completes the conversion of the 69 kV system in Hutchinson to 115 kV. | Convert the HEC - 43rd&Lorraine - Tower 33 - Meadowlark - 3rd&VanBuren 69 kV to 115 kV | TO study identified as needed June 2006. Project completes the conversion of the 69 kV system in Hutchinson to 115 kV. Required for compliance with NERC Reliability Standard TPL-002-0. See Westar Five-Year Transmission Construction Recommendations, August 12,2005, P. 23.
- | WERE | XFR - County Line 115/69 kV | 2009-07-01 | 2007-06-01 | 1700000 | Identified in the 2006 SPP Expansion Plan as needed in 2007 TPL002 | Replace existing 66 MVA 115-69 kV transformer with 112 MVA unit | To address overload issue at County Line 115 KV (57153) for the loss of Stranger Creek 345/115/14.4kV XFMR (56772/57268/56811).
Y | WERE | Line - Stranger Creek - Thornton Street 115 kV | 2009-07-01 | 2007-06-01 | 2500000 | Identified in the 2006 SPP Expansion Plan as needed in 2007 TPL002 | New 115 kV Line from Stranger Creek (57268) to Thornton Street (57272). | To address low voltage issues @ Hallmark 115 kV (57242) & Lansing 115 kV (57246) for the loss of the Jarbalo (57244) - Lansing (57246) 115 kV line. Also addresses low voltage issues @ Parallel 115 kV (57218), Walnut 115 kV (57220), Arnold 69 kV (57471), Atchison Castings 69 kV (57474), Maur Hill 69 kV (57476), Midwest Grain 69 kV (57477), Muscotah 69 kV (57480), Nortonville 69 kV (57481), Wathena 69 kV (57105) for the loss of Arnold to Stranger Creek 115 kV line. Also addresses overload issues.
- | WERE | Device - 3rd & VanBuren 115 kV | 2010-07-01 | 2008-06-01 | 500000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2008 TPL002 | Install switched capacitor bank | To address Westar voltage criteria violation at 3rd & Van Buren 115 kV (bus # 57435), 43rd & Lorraine 115 kV (bus # 57440) & Meadowlark 115 kV (bus # 57441) for the loss of Hutchinson Energy Center (bus # 57419) - 43rd & Lorraine (bus # 57440) 115 KV line.
- | WFEC | Device - Rush Springs 69 kV | 2006-06-01 | - | 90000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 6/1/2006 TPL-002 | Install switched cap 3MVar | To address low voltage @ Rush Springs due to outage of Fletcher to Marlow 69 kV line | N | N | N | N | N
- | WFEC | Line - ACME - W Norman 69 kV | 06/1/07 * | 2007-06-01 | 912000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Reconductor 3.8 miles from 3/0 ACSR to 795 ACSR. RateA=81MVA, RateB=106MVA | To relieve overload on ACME to W Norman 69 kV for outage of Canandian 138/69 kV transformer | N | N | N | N | N
- | WFEC | Device - Cashion 69 kV | 06/1/07 * | 2007-06-01 | 108000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install 2 - 3 MVAR capacitors at Cashion 69 kV bus | To address low voltage @ Cashion 69 kV for loss of Dover to Dover Junction 69 kV line
- | WFEC | Device - Comanche | 06/1/07 * | 2007-06-01 | 350000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install 12 MVAR Capacitor at Comanche 138 kV bus | Identified in Aggregate Study by Tariff Studies Group as a reliability project for the SPP Expansion Plan | N | N | N | N | N
- | WFEC | Device - Pink Southwest 138 kV | 06/1/07 * | 2007-04-01 | 216000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install 6 MVAR capacitor at Pink Southwest 138 kV bus | To address low voltage @ Pink Southwest 138 kV for outage of | N | N | N | N | N
- | WFEC | Device - Snyder | 06/1/07 * | 2007-04-01 | 100000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Upgrade 12 Mvar cap bank at Snyder to 24Mvar | Identified in Aggregate Study by Tariff Studies Group as a reliability project for the SPP Expansion Plan | N | N | N | N | N
- | WFEC | Line - Bradley - Rush Springs 69 kV | 12/1/07 * | 2007-12-01 | 1656000 | Identified in the 2006 SPP Expansion Plan as needed in 12/1/2007 TPL002 | Reconductor 6.9 miles from 1/0 ACSR to 795 ACSR. RateA=81MVA, RateB=106MVA | To relieve overload on Bradley to Rush Springs 69 kV for outage of Elmore to Wallville 69 kV line.
- | WFEC | Line - Elmore - Wallville 69 kV | 12/1/07 * | 2007-12-01 | 1488000 | Identified in the 2006 SPP Expansion Plan as needed in 12/1/2007 TPL002 | Reconductor 6.2 miles from 1/0 ACSR to 336 ACSR. RateA=47MVA, RateB=61MVA | To relieve overload for outage of Bradley to Rush Springs 69 kV line
Y | WFEC | Multi - Sayre - Morewood 138 kV | 06/1/08 * | 2008-06-01 | 12000000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2008 TPL002 | Build new 138 kV line Sayre to Erick. Convert voltage for Erick-Sweetwater-Durham-Brantley-Morewood-SW to 138 kV. Add Sayre PSO interconnect at 138 kV (assumed 15 miles of new line, 75 miles of voltage conv) | To relieve overload for outage of Morwood 69 kV line | N | N | N | N | N
* Indicates that In-Service date is assumed to be date identified in SPP Expansion Plan
|  |  |  | Total: | 103867808.22
Base Plan Upgrade recommendations identified in the Aggregates Study Process
Mw-mi | Area | Project Name | In-Service Date | 2006 Expansion Plan Date | Cost Estimate | Base Plan Reason | Project Description/Comments | Project Justification
- | AEPW | Line - Okmulgee - Weleetka 138 kV Ckt 1 | 2006-04-01 | - | 84000 | Transmission Service Request | Replace Weleetka wavetrap | per 2005-AG2
- | AEPW | Line - Cache - Snyder 138kV | 2008-06-01 | 2013-06-01 | 73348 | Transmission Service Request | Replace Snyder wavetrap | per 2006-AG1 | N | N | N | N | N
- | AEPW | Line - NW Henderson - Oak Hill 138 kV | 2008-06-01 | 2013-06-01 | 75000 | Transmission Service Request | Replace wavetrap and reset CTs @ NW Henderson. | per 2005-AG1
- | OKGE | Line - Wind Farm - Mooreland 138 kV | 2008-06-01 | 2007-06-01 | 120000 | Transmission Service Request | Upgrade conductor between Mooreland 138 and Wind Farm 138 with 795AS33 | per 2006-AG1 | Y | Y | N | N | N
- | WFEC | Line - Wind Farm - Mooreland 138 kV | 2008-06-01 | 2007-06-01 | 750000 | Transmission Service Request | Upgrade terminal equipment at Mooreland | per 2006-AG1 | N | N | N | N | N
1102348

## 2006 Apprv Base Plan List
|  | Base Plan List as of April 25, 2006 | [7 empty] | Project Completed | Engineering Completed | Obtained ROW | In Construction | Done Energized
| MW-mi | Area | Project Name | In-Service Date | 2006 Expansion Plan Date | Cost Estimate | Base Plan Reason | Project Description/Comments | Project Justification
c | - | AEPW | Line - Tontitown - Elm Springs REC 161 kV | 2006-05-01 | - | 640000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 2006 TPL002 | Rebuild line with 2-397 ACSR. Replace 1200 A switch 1045, and bus Elm Springs. | Tontitown-Elm Spring 161 kV line overload for outage of Dyess-Tontitiown 161 kV
c | - | AEPW | Device - Arsenal Hill | 2006-06-01 | - | 432000 | Required to meet Transmission owner Criteria | Install switched capacitor bank | Power factor correction, voltage support, and VAR supply. Supplying VARs to the system enables generation to reduce VAR output, so that during contingencies, generators can rapidly respond with VAR support. The AEP Transmission Planning Reliability Criteria | Y | Y | N | N | N
c | - | AEPW | Device - Catoosa | 2006-06-01 | - | 394000 | Required to meet Transmission owner Criteria | Install switched capacitor bank | Power factor correction, voltage support, and VAR supply. Supplying VARs to the system enables generation to reduce VAR output, so that during contingencies, generators can rapidly respond with VAR support. The AEP Transmission Planning Reliability Cri | Y | Y | N | N | N
c | - | AEPW | Line - Carthage REC - Carthage T 138 kV | 2006-06-01 | - | 690000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 2007 TPL002 | Reconductor line with 1272 ACSR | Carthage REC-Carthage overloads for an outage Keatchie-Stonewall 138 kV | Y | Y | N | N | N
c | Y | AEPW | Line - Siloam Springs - Chamber Springs 161 kV | 2007-05-01 | - | 6627225 | Identified in the 2004_2005 SPP Expansion Plan as needed in 6/1/2007 TPL002 | New 161 line, Terminal equipment at Chamber Spring and Siloam Springs | Flint Creek-Chamber Springs 161 kV and Flint Creek -Tontitown 161 kV overload for outage of Chamber Springs - Clarksville 345 kV | N | N | N | N | N
c | - | AEPW | Line - South Shreveport - SW Shreveport 138 kV | 2007-05-01 | - | 130000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 6/1/2010 TPL002 | Replace wavetrap at South Shreveport | To address overloads due to loss of Southwest Shreveport-Western Electric-Stonewall | N | N | N | N | N
c | - | AEPW | Line - 53rd & Garnett N. Tap - Tulsa Southeast 138 kV | 2007-06-01 | - | 63000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 6/1/2006 TPL002 | Replace 3 switches | 53rd & Garnett North Tap-Tulsa SE over load for an outage of Oneta- 12 ST. & Lynn Lane | N | N | N | N | N
c | - | AEPW | Line - Knox Lee - Oak Hill #2 138 kV | 2007-06-01 | 2010-06-01 | 100000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2010 TPL002 | Replace relay, wave trap at Knoxlee |  | N | N | N | N | N
| x | AEPW | Line - Hart's Island - Port Robson 138 kV | 2007-06-01 | - | 16397600 | Project replaced by Finney Tap - Port Robson | AEP is planning to build a new 1590 ACSR, 138 kV line, approximately 7 miles long, that will be radial (at least initially) from AEP's existing Hart's Island station in Shreveport, Louisiana. The line will feed a new 138-12.5 kV station called "Port Robs | To provide a second feed to new loads. The new loads are expected to increase beyond the level that the 69 kV system will be able to serve for single contingencies including: Overload of South Shreveport-Forbing 'T' 69 kV and Ellerbe Road-Lucas 69 kV for loss of Wallace Lake-Robson Road 69 kV or the Wallace Lake 138-69 kV autotransformer or overload of Wallace Lake-Robson Road 69 kV for loss of South Shreveport-Forbing 'T' 69 kV.
c | Y | EMDE | Line - ReinMiller - Tipton Ford 161 kV | 2007-06-01 | - | 3215000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install new 161 kV line from 292 to 393 Build 4.2 miles Terminal at both | To address Joplin transformer overload for loss of Tipton-Joplin line | N | Y | N | N | N
c | Y | GRDA | XFR - Stilwell City 161/69 kV | 2007-06-01 | - | 1800000 | TO Study - NERC TPL-002 | Install 161/69kV autotransformer at Stilwell | Voltage @ Stilwell 54521 drops to 0.90pu with loss of line 96986--96983. This area has multiple contingencies that create voltage violations according to NERC standards. This Xfmr mitigates these violations.
c | - | KCPL | Line - Tomahawk - Bendix 161 kV | 2006-12-01 | - | 528600 | Identified in the 2004_2005 SPP Expansion Plan as needed in 2006 - TPL-002 | reconductor line with 1192 acsr | Reliability project to eliminate thermal violations for contingencies SPP 2005 NERC 1A Reliability Assessments B05SP0 case, contingency KCPL CROW #10, LaCygne-West Gardner | N | N | N | N | N
c | - | KCPL | Device - South Waverly | 2007-06-01 | - | 611000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install 15 Mvar capacitor at S. Waverly 161 kV bus.
c | - | KCPL | Line - Stilwell - Antioch 161 kV | 2007-06-01 | - | 892600 | Identified in the 2004_2005 SPP Expansion Plan as needed in 6/1/2007 - TPL-002 | Reconductor 161kV line | Reliability project to eliminate thermal violations for LaCygne-West Gardner contingency KCPL 2005 Summer Peak Operating Studies, KCPL 2005 Transmission Expansion Plan | N | N | N | N | N
c | - | MIPU | Line - Craig Interconnection | 2006-06-01 | - | 75000 | TO Study - NERC TPL-002 | New interconnection with AECI at Craig 69 kV | This interconnection operated normal open, used as an emergency back up for SJLP 69kV loop. Loss of Browns Curve - Midway 69kV line produces low voltage at Craig and other adjacent substations (0.771 pu) | N | N | N | N | Y
c | Y | MIPU | Line - Nevada 161 - Nevada Plant 69 kV | 2006-10-01 | - | 536000 | TO Study - NERC TPL-002 | New Nevada Configuration - Appleton City now terminates in Nevada 161/69, new double circuit down to Nevada Plant | Loss of 69kV line from Nevada 161 sub to Metz causes overload (107% Loading) | N | N | N | N | N
c | - | OKGE | Line - Reno - Sunny Lane 69 kV | 2006-06-01 | - | 100000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 6/1/2006 TPL002 | Replace Wave Trap and CT -- new limit 1200A | Reno - Sunny Lane overload for OKGEMTL-19 Contingency | N | Y | N | N | N
c | Y | OKGE | Line - Richards Tap - Richards 138 kV | 2006-06-01 | - | 1000000 | Violations of OGE Operating Practice S3-5 | New 138 kV line | Violations of OGE Operating Practice S3-5 due to radial load at Piedmont. S3-5 documentation has been submitted to SPP in the past | Y | Y | Y | N | Y
c | - | OKGE | Line - Van Buren AVEC - VBI 69 kV | 2006-06-01 | - | 50000 | TO Study - NERC TPL-002 | Trap & CTR work increase to 1200A. | Single contingency 55294 JOHNSON to 55295 EXPOPRK 69kV in the 2007 Summer Peak model causes this overload. Violates NERC TPL-002-0 and SPP Criteria 3.4. | Y | Y | N | N | Y
c | Y | OKGE | Line - Richards - Piedmont 138 kV | 2007-06-30 | - | 3800000 | Violations of OGE Operating Practice S3-5 | New 138kV line from Piedmont to Richards. | Violations of OGE Operating Practice S3-5 due to radial load at Piedmont. S3-5 documentation has been submitted to SPP in the past | N | N | N | N | N
| x | SWPA | XFR - Norfork 161/69 kV | 2007-06-01 | - | 1300000 | SWPA is not a current tariff signature, but would like to participate in Cost Allocation under some agreement | Replace transformer with rebuilt 37 MVA XF | To address Northfork transformer overload for outage of Northfork - Viola 69 kV
c | - | SWPS | XFR - Bailey Co 115/69 kV | 2006-06-01 | - | 2200000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 2006 TPL002 | Upgrade both existing transformer | To address loss of parallel transformer | N | N | N | N | N
c | - | SWPS | XFR - Denver City 115/69 kV | 2006-06-01 | - | 2200000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 2006 TPL002 | Upgrade both existing transformer | To address loss of parallel transformer | N | N | N | N | N
c | - | SWPS | XFR - Kress 115/69 kV | 2006-06-01 | 2007-06-01 | 1250000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/07 TPL002 | Upgrade #2 Transformer | To address loss of parallel transformer | N | N | N | N | N
c | - | SWPS | XFR - Hockley 115/69 kV | 2006-12-01 | - | 2750000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 2006 TPL002 | Upgrade both existing transformer | To address loss of parallel transformer | N | N | N | N | N
c | - | SWPS | XFR - Terry Co 115/69 kV | 2007-06-01 | - | 2375000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 2007 TPL002 | Upgrade both existing transformer | To address loss of parallel transformer | N | N | N | N | N
c | - | SWPS | XFR - Hale Co 115/69 kV | 2007-12-01 | - | 2900000 | Identified in the 2004_2005 SPP Expansion Plan as needed in 2007 TPL002 | Upgrade both existing transformer | To address loss of parallel transformer | N | N | N | N | N
c | - | WERE | Line - Circle - Hutchinson Energy Center 115 kV | 2006-04-01 | - | 300000 | TO Study Identified as Needed June 2006 | Tear down / Rebuild 0.40-mile line replacing 556.5 kcmil ACSR with 1192.5 kcmil ACSR; Project is part of a long range plan to correct service issues in the City of Hutchinson area | Overload for loss of Circle-Davis 115 kV line, NERC Reliability Standard TPL-002-0 | Y | N | N | N | N
c | - | WERE | Line - Midwest Solvent Jct 1 - Atchison Jct 2 69 kV | 2006-05-18 | - | 35000 | TO Study Identified as Needed June 2006 | Rebuild | NERC Relibility Standard TPL-002-0 _Westar 06-10 Trans Const. Rec. P12 | Y | N | N | N | N
c | Y | WERE | Multi - Morris - McDowell | 2006-07-19 | - | 7224000 | TO Study Identified as Needed June 2006 | Convert Morris County - McDowell Creek line to 230 kV operation; Construct McDowell Creek 230 kV substation and install 280 MVA 230-115 kV transformer; 230 kV ring bus substation work required at Morris County. | See Westar Five-Year Transmission Construction Recommendations, August 12,2005, P. 8 | Y | Y | N | Y | N
c | Y | WERE | XFR - Butler 138/69 kV | 2006-08-01 | - | 1600000 | TO Study Identified as Needed November 2006 | Transformer will now be installed at Butler substation instead of Midian See email from Don Taylor 10/28/05 | New load requires this transformer addition; Required for compliance with NERC Reliability Standard TPL-002-0 | N | N | N | Y | N
c | - | WERE | Device - Clearwater | 2006-12-31 | - | 1000000 | TO Study Identified as Needed Decemberr 2006 | Install switched capacitor bank at the new Clearwater 138 kV substation | NERC Reliability Standard TPL-002-0 - See Westar Energy Five-Year Transmission Construction Recommendations, August 12,2005, P. 15 | N | N | N | N | N
c | - | WERE | Device - UDALL 2 | 2006-12-31 | - | 525000 | TO Study Identified as Needed Decemberr 2006 | Install switched capacitor bank | NERC Reliability Standard TPL-002-0_Westar 5y_Trans_Const_Recomendation 2006-2010 p15-16 | N | N | N | N | N
c | - | WERE | Multi - HEC - 43rd & Lorraine - Tower 33 69 kV | 2006-12-31 | - | 2400000 | TO Study Identified as Needed December 2006 | Tear down / rebuild 5.20-mile 69 kV line as 115 kV. 69 kV system in Hutchinson will be converted to 115 kV by fall 2008. | Required for compliance with NERC Reliability Standard TPL-002-0. The project eliminates Transmission Operating Directives when the conversion to 115 kV is complete in fall 2008. This construction and rebuilding of substations are interlinked to provide | N | N | N | N | N
c | - | WERE | Device - NE Parsons | 2007-06-01 | 2007-06-01 | 1000000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install switched capacitor bank | NERC Reliability Standard TPL-002-0_Westar 5y_Trans_Const_Recomendation 2006-2010 p14 | N | N | N | N | N
c | - | WERE | Device - Parsons | 2007-07-01 | 2007-06-01 | 525000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install switched capacitor bank | NERC Reliability Standard TPL-002-0 _Westar 5y_Trans_Const_Recomendation 2006-2010 p13 | N | N | N | N | N
c | - | WERE | Device - Nortonville 69 kV Cap | - | 2007-06-01 | 564000 | Identified in the 2006 SPP Expansion Plan as needed in 6/1/2007 TPL002 | Install 15 Mvar cap at Nortonville 69 kV (bus #57481) | NERC Reliability Standard TPL-002-0_Westar 5y_Trans_Const_Recomendation 2006-2010 p18 | N | N | N | N | N
| x | WERE | XFR - Weaver 138/69 kV | 2010-07-01 | 2010-07-01 | 1200000 | Project pushed back to 2010 for reliability need | New transformer #2 at Weaver | To address ineffective operating guide in 2010
| - | WFEC | Device - Dover | - | 2015-06-01 | 90000 | Project is being replaced by Rush Springs Cap | Add 3 MVAR switched capacitor at Rush Springs 69 kV bus. | Low Voltage around Dover for loss of Dover XF
[5 empty] | Total: | 50532425
Note on B19: ccc1103: Under 100k, direct assign

## Resident Loads
AVERAGE PEAK LOAD
ZONE | Members/Customer | 2005-01-01 | 2005-02-01 | 2005-03-01 | 2005-04-01 | 2005-05-01 | 2005-06-01 | 2005-07-01 | 2005-08-01 | 2005-09-01 | 2005-10-01 | 2005-11-01 | 2005-12-01 | 2005 Avg
AEP | AEP_PSO_SWEPCO_TNC | 6063 | 5694 | 5351 | 5417 | 7291 | 8391 | 8631 | 8594 | 8429 | 7167 | 5652 | 6733 | 6951.0833
AEP | ETEC | 73 | 67 | 54 | 35 | 55 | 75 | 70 | 75 | 74 | 56 | 63 | 85 | 65.1667
AEP | NTEC | 606 | 566 | 486 | 405 | 502 | 623 | 603 | 619 | 484 | 478 | 534 | 682 | 549
AEP | TXLA | 55 | 45 | 42 | 56 | 76 | 99 | 78 | 89 | 102 | 91 | 78 | 97 | 75.6667
AEP | OMPA_PSO | 72 | 69 | 63 | 79 | 124 | 146 | 148 | 148 | 135 | 114 | 71 | 86 | 104.5833
AEP | GOLDEN SPREAD | 5 | 6 | 5 | 3 | 5 | 5 | 9 | 6 | 7 | 4 | 4 | 6 | 5.4167
TOTAL AEP ZONE |  | 6874 | 6447 | 6001 | 5995 | 8053 | 9339 | 9539 | 9531 | 9231 | 7910 | 6402 | 7689 | 7750.9167 | 26.84%
AQUILA_MPS_SJLP | AQUILA_MPS | 1289 | 1192 | 1087 | 961 | 1306 | 1704 | 1826 | 1800 | 1549 | 1403 | 1210 | 1422 | 1395.75 | 4.834%
AQUILA_WPEK | AQUILA_WPEK | 398 | 377 | 361 | 364 | 492 | 467 | 487 | 476 | 448 | 460 | 338 | 356 | 418.6667 | 1.45%
EDME | EDME | 900 | 820 | 818 | 622 | 820 | 1033 | 1087 | 1050 | 991 | 854 | 837 | 1031 | 905.25
EDME | KEPCO | 3 | 3 | 3 | 2 | 3 | 4 | 5 | 4 | 4 | 3 | 3 | 4 | 3.4167
TOTAL EDME ZONE |  | 903 | 823 | 821 | 624 | 823 | 1037 | 1092 | 1054 | 995 | 857 | 840 | 1035 | 908.6667 | 3.147%
GRDA | GRDA | 582 | 559 | 537 | 529 | 669 | 844 | 910 | 867 | 823 | 555 | 567 | 652 | 674.5 | 2.336%
KCPL | KACP | 2313 | 2186 | 2003 | 2042 | 2615 | 3338 | 3512 | 3426 | 3007 | 2754 | 2209 | 2563 | 2664 | 9.226%
MIDW | MIDW | 200 | 185 | 176 | 177 | 261 | 303 | 320 | 322 | 271 | 247 | 191 | 217 | 239.1667
| MIDW_KEPCo | 6 | 6 | 5 | 5 | 9 | 13 | 16 | 14 | 9 | 8 | 7 | 9 | 8.9167
TOTAL MIDW ZONE |  | 206 | 191 | 181 | 182 | 270 | 316 | 336 | 336 | 280 | 255 | 198 | 226 | 248.0833 | 0.8592%
OKGE | OKGE | 3970 | 3682 | 3389 | 3502 | 4941 | 5445 | 5725 | 5584 | 5378 | 4572 | 3609 | 4345 | 4511.8333
OKGE | OMPA_OGE | 221 | 191 | 175 | 225 | 353 | 387 | 420 | 406 | 379 | 313 | 217 | 262 | 295.75
OKGE | WFEC_OGE | 84 | 73 | 57 | 50 | 82 | 95 | 96 | 103 | 92 | 78 | 73 | 94 | 81.4167
TOTAL OKGE ZONE | OKGE Total | 4275 | 3946 | 3621 | 3777 | 5376 | 5927 | 6241 | 6093 | 5849 | 4963 | 3899 | 4701 | 4889 | 16.93%
SPRM | SPRM | 438 | 417 | 403 | 425 | 539 | 686 | 720 | 688 | 642 | 551 | 429 | 475 | 534.4167 | 1.851%
SWPS | SWPS | 3411 | 3372 | 3264 | 3494 | 4397 | 4798 | 4978 | 4870 | 4162 | 3771 | 3418 | 3838 | 3981.0833 | 13.79%
SUNF | SUNF | 304 | 283 | 281 | 276 | 363 | 399 | 420 | 412 | 363 | 346 | 287 | 301 | 336.25 | 1.164%
WEFA | OMPA_WFEC | 21 | 19 | 17 | 17 | 29 | 31 | 34 | 34 | 32 | 26 | 19 | 22 | 25.0833
WEFA | WEFA | 1086 | 968 | 873 | 743 | 1084 | 1197 | 1236 | 1210 | 1152 | 989 | 957 | 1226 | 1060.0833
WEFA | WEFA_LINDSEY | 4 | 3 | 3 | 4 | 6 | 7 | 8 | 7 | 7 | 5 | 3 | 4 | 5.0833
TOTAL WFEA ZONE |  | 1111 | 990 | 893 | 764 | 1119 | 1235 | 1278 | 1251 | 1191 | 1020 | 979 | 1252 | 1090.25 | 3.776%
WESTAR | KEPCO | 167 | 184 | 156 | 112 | 173 | 253 | 270 | 253 | 225 | 184 | 192 | 227 | 199.6667
WESTAR | KPP | 68 | 62 | 54 | 67 | 85 | 88 | 102 | 100 | 98 | 96 | 76 | 82 | 81.5
WESTAR | Westar_KGE_KPL | 3047 | 3025 | 2666 | 2992 | 3852 | 4515 | 4672 | 4704 | 4385 | 3951 | 3147 | 3475 | 3702.5833
TOTAL WESTAR ZONE |  | 3282 | 3271 | 2876 | 3171 | 4110 | 4856 | 5044 | 5057 | 4708 | 4231 | 3415 | 3784 | 3983.75 | 13.8%
|  | 25386 | 24054 | 22329 | 22604 | 30132 | 34946 | 36383 | 35861 | 33248 | 29076 | 24191 | 28294 | 28875.3333 | 100%
ZONE
CLECO
SWPA
| AEP | 26.84% | 7750.9167
| GRDA | 2.336% | 674.5
| OKGE | 16.93% | 4889
| WFEC | 3.776% | 1090.25
| SPS | 13.79% | 3981.0833
| MIDW | 0.8592% | 248.0833
| SUNF | 1.164% | 336.25
| WESTAR | 13.8% | 3983.75
| WEPL | 1.45% | 418.6667
| MIPU | 4.834% | 1395.75
| KACP | 9.226% | 2664
| EMDE | 3.147% | 908.6667
| SPRM | 1.851% | 534.4167
| TOTAL | 100% | 28875.3333
Note on B5: rds0500: information source is Pennybaker analysis of transmission system demands.
Note on B6: rds0500: As reported by AEP
Note on B7: rds0500: As reported by AEP
Note on B8: rds0500: As reported by AEP
Note on B9: rds0500: Used AEP Version. Slightly different numbers reported by OMPA. OMPA note indicated possible revision would be necessary
Note on B10: rds0500: Includes Green belt and Lignthouse - Served from Texas North facilities in SPP
Note on B13: rds0500: Includes St. Joe
Note on B17: rds0500: Agrees with SPP NITS Billing.
Note on B18: rds0500: Per SPP NITS Billings
Note on B21: rds0500: GRDA reported numbers exclude Lindsey, Broken Bow and KAMO Ties to SPP NITS Billing
Note on B23: rds0500: No SPP NITS in KCPL
Note on B25: rds0500: Agrees with MIDW EIA-411. Off slightly from loads reported by Westar Energy
Note on B26: rds0500: From SPP NITS Billing
Note on B29: rds0500: Ties to Kays' analysis of transmission system load.
Note on B34: rds0500: Use Assessment loads
Note on B36: rds0500: Includes all SPS load per Bob Cochrane 6-23-06.
Note on B40: rds0500: Reported by OMPA
Note on B41: rds0500: Reported by WFEC, Check to see that it excludes Broken Bow and Lindsey
Note on B42: rds0500: Reported by GRDA

## FCRs
|  | A. Weighted Cost of Capital | B. Depreciation Rate for Transmission | C. Composite Income Tax Expense | D. Rate for Other Tax Expense | E. Rate for Administrative & General Expense | F. Rate for Operation & Maintenance Expense | G. Rate for Allocation of General Plant | H. Deferred Income Tax Adjustment | Total Fixed Charge Rate (A+B+C+D+E+F+G-H)
AEP | American Electric Power West | 8.59% | 3.333% | 2.24% | 1.59% | 0.52% | 2.56% | 0.26% | -1.08% | 18.01%
CLECO | Central Louisiana Electric Company (1) | 9.667% | 0% | 3.471% | 2.411% | 0.6101% | 1.674% | 0.3549% | -1.314% | 16.87%
EMDE | Empire District Electric | 9.08% | 3.333% | 2.76% | 1.56% | 0.86% | 1.64% | 0.25% | -1.18% | 18.3%
GRDA | Grand River Dam Authority | 10.95% | 3.333% | 0% | 0% | 1.48% | 2.78% | 0.5% | 0% | 19.04%
KACP | Kansas City Power & Light Company | 9.22% | 3.333% | 2.86% | 2.18% | 1.4% | 4.17% | 0.33% | -1.21% | 22.28%
MIDW | Midwest Energy | 7.81% | 3.333% | 0% | 1.67% | 0.6% | 1.69% | 0.16% | -0.78% | 14.48%
MIPU | Missouri Public Service (Aquila) | 9.04% | 3.333% | 2.82% | 1.14% | 0.81% | 1.42% | 0.11% | -1.19% | 17.48%
OKGE | OG+E Electric Services | 9.59% | 3.333% | 3.42% | 1.09% | 1.43% | 4.38% | 0.41% | -1.3% | 22.35%
SWPA | Southwestern Power Administration | 6.62% | 3.333% | 0% | 0% | 2.298% | 6.363% | 0% | 0% | 18.61%
SPS | Southwestern Public Service (XCEL) | 8.37% | 3.333% | 2.3% | 1.44% | 0.79% | 1.25% | 0.29% | -1.07% | 16.7%
SPRM | City Utilities, Springfield | 8.1% | 3.333% | 0% | 0.83% | 0.82% | 2.46% | 0.13% | 0% | 15.67%
SUNF | Sunflower (Tariff participant 4/1/06) | 5.98% | 3.333% | 0% | 0% | 0.81% | 6.01% | 0.15% | -0.6% | 15.68%
| St. Joes Light and Power (Aquila) | 9.87% | 3.333% | 3.03% | 1.39% | 2.2% | 4.66% | 0.42% | -1.29% | 23.61%
WEPL | West Plains (Aquila) | 9.47% | 3.333% | 2.64% | 1.71% | 1.09% | 1.93% | 0.16% | -1.21% | 19.12%
WESTAR | Western Farmers Electric Coop. | 4.406% | 3.333% | 0% | 0% | 0.496% | 3.019% | 0.094% | 0% | 11.35%
WFEC | Westar Energy | 7.53% | 3.333% | 2.7% | 1.56% | 1.4% | 2.35% | 0.39% | -1.02% | 18.24%
Note on B2: jbr0903: Updated based on 2004 Form 1 data on 4/5/06
Note on B4: jbr0903: updated 4/27/06. EDE ROE is what was filed not approved.
Note on B6: jbr0903: Updated 6/9/06
Note on B7: jbr0903: Updated on 4/13/06
Note on B8: jbr0903: updated 7/18/05
Note on B9: jbr0903: Updated 4/26/06
Note on B11: jbr0903: Revised 5/15/06
Note on B13: jbr0903: Updated 4/6/06
Note on B14: jbr0903: updated 7/18/05
Note on B15: jbr0903: updated 7/18/05
Note on B17: jbr0903: Updated 5/1/2006