RATINGS AS OF 1/17/2006

Below are the OFFICIAL ATC limits for use on the SPPSPSTIES(import), SPSSPPTIES(export), and SPSNorth-South flowgates and any re-rates due to specific operating conditions:

SPPSPSTIES 
     System intact (all ties in-service):  487 MW 
     Potter-Finney 345kV out of service:   102 MW 
     Tuco-Oklaunion 345kV out of service and both Tolk units online:   78 MW 
     Tuco-Oklaunion 345kV out of service and one Tolk units offline and the other Tolk unit limited to 450MW:   168 MW 
          (SPS has an op-guide to limit the one remaining Tolk unit to 450MW during this outage-SEE SPP Op Guides)

SPSSPPTIES 
     System intact (all ties in-service):  529 MW 
     Potter-Finney 345kV out of service:   265 MW 
     Tuco-Oklaunion 345kV out of service:  346 MW

SPSNorth-South 
     System intact (all ties in-service):  800 MW 
     Potter-Finney 345kV out of service:   600 MW 
     Tuco-Oklaunion 345kV out of service:  600 MW

IMPORT VOLTAGE STABILITY 
The SPPSPSTIES numbers are based upon a voltage stability limit which would occur at an import level of 1027 MW.  Assuming that in a normal situation, all their tie lines would be in-service and one of the Tolk units is at it's PMAX of 540MW, a TRM has been assigned of 540, which limits the import to (1027-540=487) MW.  During an outage of Potter-Finney, the voltage collapse occurs at an import level of 642 MW.  So with a TRM of 540, the import during this outage is limited to (642-540=102) MW.  A similar situation occurs during an outage of Tuco-Oklaunion 345kV.  The import limit maximum is 618 MW, but (with 540MW TRM for loss of Tolk) is limited to 78 MW ATC.  However, SPS has an operating guide that says during the outage of Tuco-Oklaunion, if one of the Tolk units is offline, the other unit is limited to 450 MW.  This affects the TRM calculation such that the new limit is (618-450=168) MW.  Caution:  If BOTH Tolk units are online and one is operating at 540 MW, the import limit is 78 MW.  Only in the special condition that one of the Tolk units is offline can the higher limit of 168 MW be used.