## Table 1
Study Case | From Area | To Area | Monitored Branch Over 100% Rate B | Monitored Branch Over 100% Rate B | Rate <MVA> | BC % Loading | TC % Loading | Outaged Branch Causing Overload | Outaged Branch Causing Overload | ATC (MW) | Solution | Cost
04G | WERE | WERE | ATHENS SWITCHING STATION - COFFEY COUNTY NO. 4 VERNON 69KV | 57631 CC4VERN2 69 to 57623 ATHENS 2 69 CKT 1 | 45 | 104.4807 | 105.7617 | LACYGNE - WOLF CREEK 345KV | 56797 WOLFCRK7 345 to 57981 LACYGNE7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04G | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 118.5007 | 118.8464 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04G | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 102.6672 | 102.9224 | IATAN - ST JOE 345KV | 57982 IATAN 7 345 to 59199 ST JOE 3 345 CKT 1 | 0 | Rebuild 15.50-mile line (1192.5 kcmil 45/7 ACSR, 223 MVA, 245 MVA), Replace CTs and Wave Trap (2000 A.) | 5800000
04G | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 100.7079 | 100.8403 | CONCORDIA - EAST MANHATTAN 230KV | 56861 EMANHAT6 230 to 58758 CONCORD6 230 CKT 1 | 0 | See Previous Upgrade Specified
04G | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 100.6566 | 100.8037 | CONCORDIA 230/115KV TRANSFORMER | 58757 CONCORD3 115 to 58758 CONCORD6 230 CKT 1 | 0 | See Previous Upgrade Specified
04G | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 113.4655 | 113.8263 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04G | WERE | WERE | COFFEY COUNTY NO. 4 VERNON - GREEN 69KV | 57636 GREEN 2 69 to 57631 CC4VERN2 69 CKT 1 | 45 | 105.7467 | 107.0278 | LACYGNE - WOLF CREEK 345KV | 56797 WOLFCRK7 345 to 57981 LACYGNE7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04G | WERE | WERE | COFFEY COUNTY NO. 4 VERNON - GREEN 69KV | 57636 GREEN 2 69 to 57631 CC4VERN2 69 CKT 1 | 45 | 100.5435 | 101.0906 | ROSE HILL - WOLF CREEK 345KV | 56794 ROSEHIL7 345 to 56797 WOLFCRK7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04G | WERE | WERE | COFFEY COUNTY NO. 4 VERNON - GREEN 69KV | 57636 GREEN 2 69 to 57631 CC4VERN2 69 CKT 1 | 45 | 100.2507 | 100.7446 | BENTON - WOLF CREEK 345KV | 56791 BENTON 7 345 to 56797 WOLFCRK7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04G | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 111.3527 | 111.7131 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04SP | GRRD | GRRD | BRISTOW - KELLYVILLE 69KV | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 119.7607 | 120.4708 | MANFORD - SILVER CITY 69KV | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 0 | GRDA to Construct 138/69 KV Fisher Sub, tapping Keystone -- Silver City 138 KV T-line by 6/2005
04SP | SWPA | ENTR | BULL SHOALS - MIDWAY 161KV | 52660 BULL SH5 161 to 99825 5MIDWAY# 161 CKT 1 | 162 | 102.0335 | 102.2531 | INDEPENDENCE - MOOREFIELD 161KV | 99817 5ISES 1 161 to 99826 5MORFLD 161 CKT 1 | 0 | Replace disconnect switches, metering CTs and wave trap at Bull Shoals. | 150000
04SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 112.2195 | 112.601 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
04SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 109.6978 | 110.0692 | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
04SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 106.0875 | 106.4427 | SUB 382 - LARUSSEL - SUB 383 - MONETT 161KV | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
04SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 104.415 | 104.7802 | JASPER - LAMAR 69KV | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
04SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 101.9049 | 102.2296 | SUB 124 - AURORA H.T. - SUB 355 - AURORA WEST 69KV | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
04SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 335 | 102.9049 | 103.0777 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | Replace Farmington switch 8839 | 60000
04SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 132.3868 | 133.2241 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | Rebuild 12 miles with 2156MCM ACSR. Replace Chamber Springs wavetrap & reset relays. | 7200000
04SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 244 | 122.3263 | 122.842 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 118.6957 | 119.5398 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 100.2142 | 100.8617 | FLINT CREEK - GENTRY REC 161KV | 53139 FLINTCR5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SP | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 84 | 106.6162 | 106.6958 | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 0 | Add 3rd 161/69 KV Transformer | 1250000
04SP | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 84 | 106.9349 | 107.0149 | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 0 | See Previous Upgrade Specified
04SP | OMPA | AEPW | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 56204 OMDUNCN4 138 to 54157 COMMTAP4 138 CKT 1 | 117 | 105.7062 | 106.6745 | CORNVILLE - RUSH SPRINGS NATURAL GAS TAP 138KV | 54112 CORNVIL4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | Rebuild 17.81 miles of 266 ACSR with 795 ACSR | 6100000
04SP | AEPW | AEPW | DYESS - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53131 DYESS 5 161 CKT 1 | 313 | 100.9179 | 101.0027 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | Replace South Springdale Circuit Switcher & Jumpers | 60000
04SP | GRDA | GRDA | KINZIE 138/69KV TRANSFORMER | 54510 KINZEGR4 138 to 54513 KINZEGR2 69 CKT 1 | 56 | 112.2145 | 112.3645 | CENTRAL - STILLWATER 69KV | 54453 CENTRL 2 69 to 96845 2STILWTR 69 CKT 1 | 0 | Solution Undetermined
04SP | GRDA | GRDA | TAHLEQUAH 161/69KV TRANSFORMER CKT 1 | 54455 TAHLQH 5 161 to 54447 TAHLQH 2 69 CKT 1 | 78 | 107.5648 | 108.8961 | TAHLEQUAH 161/69KV TRANSFORMER CKT 2 | 54447 TAHLQH 2 69 to 54455 TAHLQH 5 161 CKT 2 | 0 | Add 3rd 161/69 KV Transformer | 1400000
04SP | GRDA | GRDA | TAHLEQUAH 161/69KV TRANSFORMER CKT 2 | 54455 TAHLQH 5 161 to 54447 TAHLQH 2 69 CKT 2 | 78 | 109.067 | 109.4934 | TAHLEQUAH 161/69KV TRANSFORMER CKT 1 | 54447 TAHLQH 2 69 to 54455 TAHLQH 5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SP | AEPW | AEPW | EAST CENTRAL HENRYETTA - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54049 EC.HEN-4 138 CKT 1 | 105 | 92.7795 | 105.0684 | KELCO - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54057 KELCO 4 138 CKT 1 | 705.0769 | Replace Okmulgee Wavetrap | 40000
04SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 99.4431 | 100.0887 | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 1035.1199 | See Previous Upgrade Specified
04SP | AEPW | AEPW | EAST CENTRAL HENRYETTA - WELEETKA 138KV | 54049 EC.HEN-4 138 to 54028 WELETK4 138 CKT 1 | 105 | 88.5803 | 100.8672 | KELCO - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54057 KELCO 4 138 CKT 1 | 1115.3048 | Replace Weleetka Wavetrap | 40000
04SP | AEPW | AEPW | ATOKA - ATOKA PUMP 69KV | 54004 ATOKA P2 69 to 54007 ATOKA--2 69 CKT 1 | 39 | 116.9999 | 117.0832 | LONE OAK - SOUTH MCALESTER TAP 138KV | 54022 LONEOAK4 138 to 54032 SMCALTP4 138 CKT 1 | 1200 | Invalid Contingency
04SP | AEPW | AEPW | MCALESTER - WELEETKA 69KV | 54024 MCALEST2 69 to 54029 WELEETK2 69 CKT 1 | 52 | 119.9831 | 120.3934 | LONE OAK - SOUTH MCALESTER TAP 138KV | 54022 LONEOAK4 138 to 54032 SMCALTP4 138 CKT 1 | 1200 | Invalid Contingency
04SP | SWPA | SWPA | SPRINGFIELD 161/69KV TRANSFORMER CKT 3 | 52694 SPRGFLD269.0 WND 1 SPF X3 1 | 25 | 100.2005 | 100.5317 | SPRINGFIELD 161/69KV TRANSFORMER CKT 1 | 52692 SPRGFLD5 161 to 52694 SPRGFLD269.0 to 52691 SPF X1 113.8 CKT 1 | 1200 | An outage of Springfield transformer #1 overloads transformer #3. If this situation were to occur, SWPA would open either the high or low side breaker on transformer #3 to remove the overload. This does not introduce any other overloads.
04SH | WERE | WERE | ANZIO - FORT JCT SWITCHING STATION 115KV | 57321 ANZIO 3 115 to 57328 FT JCT 3 115 CKT 1 | 92 | 100.1508 | 100.3527 | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57342 WJCCTY 3 115 to 57343 WJCCTYE3 115 CKT 1 | 0 | Solution Undetermined
04SH | WERE | WERE | ANZIO - FORT JCT SWITCHING STATION 115KV | 57321 ANZIO 3 115 to 57328 FT JCT 3 115 CKT 1 | 92 | 100.1472 | 100.349 | Multiple Outage Contingency: FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | Multiple Outage Contingency: 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 0 | May be relieved due to Westar Transmission Operating Directive 1217 Outage of the Fort JCT-West JCT City 115kV Line
04SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 105.9603 | 106.2001 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
04SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 103.5084 | 103.748 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
04SH | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 109.0465 | 109.7419 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SH | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 244 | 100.4446 | 100.9278 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SH | GRDA | GRDA | KINZIE 138/69KV TRANSFORMER | 54513 KINZEGR2 69 to 54510 KINZEGR4 138 CKT 1 | 56 | 108.9048 | 109.0936 | CENTRAL - STILLWATER 69KV | 54453 CENTRL 2 69 to 96845 2STILWTR 69 CKT 1 | 0 | Solution Undetermined
04SH | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57343 WJCCTYE3 115 to 57328 FT JCT 3 115 CKT 1 | 68 | 102.6653 | 102.9325 | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 1200 | Invalid Contingency
04FA | WERE | WERE | ATHENS SWITCHING STATION - COFFEY COUNTY NO. 4 VERNON 69KV | 57631 CC4VERN2 69 to 57623 ATHENS 2 69 CKT 1 | 45 | 107.6192 | 107.8365 | LACYGNE - WOLF CREEK 345KV | 56797 WOLFCRK7 345 to 57981 LACYGNE7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04FA | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 117.4023 | 117.7189 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04FA | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 112.3127 | 112.6434 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04FA | WERE | WERE | COFFEY COUNTY NO. 4 VERNON - GREEN 69KV | 57636 GREEN 2 69 to 57631 CC4VERN2 69 CKT 1 | 45 | 108.8919 | 109.1068 | LACYGNE - WOLF CREEK 345KV | 56797 WOLFCRK7 345 to 57981 LACYGNE7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04FA | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 110.2001 | 110.5306 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 124.5347 | 124.7323 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 105.4587 | 105.7279 | IATAN - ST JOE 345KV | 57982 IATAN 7 345 to 59199 ST JOE 3 345 CKT 1 | 0 | See Previous Upgrade Specified
04WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 101.011 | 101.2366 | CONCORDIA - EAST MANHATTAN 230KV | 56861 EMANHAT6 230 to 58758 CONCORD6 230 CKT 1 | 0 | See Previous Upgrade Specified
04WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 100.9605 | 101.1866 | CONCORDIA 230/115KV TRANSFORMER | 58757 CONCORD3 115 to 58758 CONCORD6 230 CKT 1 | 0 | See Previous Upgrade Specified
04WP | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 121.2458 | 121.4524 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04WP | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 101.2154 | 101.4972 | IATAN - ST JOE 345KV | 57982 IATAN 7 345 to 59199 ST JOE 3 345 CKT 1 | 0 | Rebuild 15.15 mile line with 1192.5 kcmil ACSR. | 3200000
04WP | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 119.3634 | 119.5699 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04WP | SWPA | SWPA | NORFORK 161/69KV TRANSFORMER CKT 1 | 52648 NORFORK5 161 WND 2 NFK X1 1 | 25 | 109.8084 | 109.8761 | NORFORK 161/69KV TRANSFORMER CKT 2 | 52648 NORFORK5 161 to 52650 NORFORK269.0 to 52651 NFK X2 113.8 CKT 1 | 0 | Replace Norfork Transformer | 1300000
04WP | SWPA | SWPA | NORFORK 161/69KV TRANSFORMER CKT 1 | 52650 NORFORK269.0 WND 1 NFK X1 1 | 25 | 109.0293 | 109.0945 | NORFORK 161/69KV TRANSFORMER CKT 2 | 52648 NORFORK5 161 to 52650 NORFORK269.0 to 52651 NFK X2 113.8 CKT 1 | 0 | See Previous Upgrade Specified
04WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 100.4638 | 100.7595 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | Tear down double circuit, build single circuit with 1192.5 ACSR. | 7800000
04WP | WERE | WERE | EL PASO - GILL ENERGY CENTER SOUTH 138KV | 57039 ELPASO 4 138 to 57046 GILL S 4 138 CKT 1 | 210 | 108.5813 | 108.8353 | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV | 57040 EVANS N4 138 to 57041 EVANS S4 138 CKT 1 | 1200 | Invalid Contingency
05AP | AEPW | CELE | INTERNATIONAL PAPER - WALLACE LAKE 138KV | 53461 WALLAKE4 138 to 50090 IPAPER 4 138 CKT 1 | 236 | 100.2983 | 101.6457 | DOLET HILLS 345/230KV TRANSFORMER | 50045 DOLHILL7 345 to 50046 DOLHILL6 230 CKT 1 | 0 | May be relieved by Dolet Hills Operating Guide
05AP | AEPW | AEPW | SOUTH SHREVEPORT - WALLACE LAKE 138KV | 53446 S SHV 4 138 to 53461 WALLAKE4 138 CKT 1 | 210 | 103.5951 | 104.9024 | DOLET HILLS 345/230KV TRANSFORMER | 50045 DOLHILL7 345 to 50046 DOLHILL6 230 CKT 1 | 0 | May be relieved by Dolet Hills Operating Guide
05G | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 118.3568 | 118.4866 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05G | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 113.063 | 113.1986 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05G | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 110.8862 | 111.0216 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05G | WERE | WERE | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JCT (SOUTH) 115KV | 57372 PHILIPS3 115 to 57374 SPHILPJ3 115 CKT 1 | 160 | 101.3986 | 101.5851 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | Rebuild 0.88 miles and reconductor with 1192.5 ACSR. | 417200
05G | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 109.4566 | 109.6565 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05G | WERE | WERE | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57343 WJCCTYE3 115 to 57342 WJCCTY 3 115 CKT 1 | 141 | 100.008 | 100.1209 | JEFFREY ENERGY CENTER - SUMMIT 345KV | 56766 JEC N 7 345 to 56773 SUMMIT 7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 402 Outage of the Jeffrey Energy Center to Summit 345 kV Line
05G | WERE | WERE | EL PASO - GILL ENERGY CENTER SOUTH 138KV | 57039 ELPASO 4 138 to 57046 GILL S 4 138 CKT 1 | 210 | 125.0947 | 125.2507 | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV | 57040 EVANS N4 138 to 57041 EVANS S4 138 CKT 1 | 1200 | Invalid Contingency
05G | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57343 WJCCTYE3 115 to 57328 FT JCT 3 115 CKT 1 | 68 | 104.8121 | 104.9402 | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 1200 | Invalid Contingency
05SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 152.6895 | 152.8014 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 147.8016 | 147.9723 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 133.5397 | 133.6375 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 129.2755 | 129.4248 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 112.7228 | 113.0773 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
05SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 108.9382 | 109.2865 | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
05SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 107.3321 | 107.6239 | SUB 382 - LARUSSEL - SUB 383 - MONETT 161KV | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
05SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 103.6568 | 104.0031 | JASPER - LAMAR 69KV | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
05SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 101.9003 | 102.1912 | SUB 124 - AURORA H.T. - SUB 355 - AURORA WEST 69KV | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
05SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 101.2727 | 101.4264 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 100.2918 | 100.4466 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 101.3604 | 101.5176 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | Rebuild 10.24 miles with 2156 ACSR, replace Chamber Springs wavetrap, & replace Farmington AECC bus. | 6400000
05SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 137.9994 | 138.8454 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 127.2473 | 127.7733 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 123.6495 | 124.503 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 104.6751 | 105.3335 | FLINT CREEK - GENTRY REC 161KV | 53139 FLINTCR5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 103.8508 | 104.5095 | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 84 | 107.0107 | 107.0801 | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 0 | See Previous Upgrade Specified
05SP | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 84 | 107.3275 | 107.3973 | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 0 | See Previous Upgrade Specified
05SP | OMPA | AEPW | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 56204 OMDUNCN4 138 to 54157 COMMTAP4 138 CKT 1 | 117 | 109.7694 | 110.6415 | CORNVILLE - RUSH SPRINGS NATURAL GAS TAP 138KV | 54112 CORNVIL4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
05SP | OMPA | AEPW | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 56204 OMDUNCN4 138 to 54157 COMMTAP4 138 CKT 1 | 117 | 100.1623 | 101.0329 | RUSH SPRINGS NATURAL GAS TAP - RUSH SPRINGS TAP 138KV | 54154 RUSHSPT4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
05SP | AEPW | AEPW | DYESS - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53131 DYESS 5 161 CKT 1 | 313 | 104.8129 | 104.8859 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57309 WEMPORI3 115 to 57301 EAST ST3 115 CKT 1 | 92 | 108.4841 | 108.619 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
05SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 101.7346 | 101.8427 | LOWELL - TONTITOWN 161KV | 53144 LOWELL 5 161 to 53170 TONTITN5 161 CKT 1 | 0 | Rebuild 1.09 miles of 2-397.5 ACSR with 2156 ACSR. Replace Flint Creek wavetrap & jumpers | 450000
05SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 143.9578 | 144.0692 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 139.3217 | 139.4915 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 126.0237 | 126.1212 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 121.9117 | 122.0603 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | GRDA | GRDA | KINZIE 138/69KV TRANSFORMER | 54510 KINZEGR4 138 to 54513 KINZEGR2 69 CKT 1 | 56 | 116.405 | 116.5676 | CENTRAL - STILLWATER 69KV | 54453 CENTRL 2 69 to 96845 2STILWTR 69 CKT 1 | 0 | Solution Undetermined
05SP | WERE | WERE | LAWRENCE HILL 230/115KV TRANSFORMER | 56853 LAWHILL6 230 WND 1 LAWHL29X 1 | 308 | 107.193 | 107.2736 | LAWRENCE HILL - MIDLAND JCT 230KV CKT 1 | 56853 LAWHILL6 230 to 56855 MIDLAND6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 901 Outage of the Lawrence Hill-Midland JCT 230kV Line
05SP | WERE | WERE | LAWRENCE HILL 230/115KV TRANSFORMER | 57250 LWRNCHL3 115 WND 2 LAWHL29X 1 | 308 | 105.2471 | 105.3279 | LAWRENCE HILL - MIDLAND JCT 230KV CKT 1 | 56853 LAWHILL6 230 to 56855 MIDLAND6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 901 Outage of the Lawrence Hill-Midland JCT 230kV Line
05SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 129.9402 | 130.051 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 125.7908 | 125.9588 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 113.4738 | 113.5706 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 109.8447 | 109.9914 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 132.1608 | 132.2716 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 128.0543 | 128.2228 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 115.4804 | 115.5769 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 111.8484 | 111.9956 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | AEPW | AEPW | BLUE CIRCLE - CATOOSA 69KV | 53806 BCIRCLE2 69 to 53811 CATOOSA2 69 CKT 1 | 72 | 101.8954 | 102.1563 | LYNN LANE TAP - LYNN LANE WEST TAP 138KV | 53782 LLAN WT4 138 to 53816 LLANETP4 138 CKT 1 | 1200 | Invalid Contingency
05SP | AEPW | AEPW | MCALESTER - WELEETKA 69KV | 54024 MCALEST2 69 to 54029 WELEETK2 69 CKT 1 | 52 | 127.0412 | 127.4195 | LONE OAK - SOUTH MCALESTER TAP 138KV | 54022 LONEOAK4 138 to 54032 SMCALTP4 138 CKT 1 | 1200 | Invalid Contingency
05SH | WERE | WERE | ANZIO - FORT JCT SWITCHING STATION 115KV | 57321 ANZIO 3 115 to 57328 FT JCT 3 115 CKT 1 | 92 | 103.0172 | 103.1868 | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57342 WJCCTY 3 115 to 57343 WJCCTYE3 115 CKT 1 | 0 | Solution Undetermined
05SH | WERE | WERE | ANZIO - FORT JCT SWITCHING STATION 115KV | 57321 ANZIO 3 115 to 57328 FT JCT 3 115 CKT 1 | 92 | 103.0122 | 103.1817 | Multiple Outage Contingency: FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | Multiple Outage Contingency: 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 0 | May be relieved due to Westar Transmission Operating Directive 1217 Outage of the Fort JCT-West JCT City 115kV Line
05SH | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 147.7527 | 147.8918 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 129.2285 | 129.3501 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 110.4321 | 110.6621 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 107.4866 | 107.7143 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 109.7852 | 110.0135 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52690 CARTHG 269.0 WND 1 CRG X2 1 | 84 | 106.6756 | 106.9012 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SH | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 115.6235 | 116.3204 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SH | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 244 | 106.5969 | 107.0796 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SH | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 244 | 103.9489 | 104.6544 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SH | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 84 | 100.2153 | 100.3878 | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 0 | See Previous Upgrade Specified
05SH | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 84 | 100.5104 | 100.6837 | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 0 | See Previous Upgrade Specified
05SH | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57309 WEMPORI3 115 to 57301 EAST ST3 115 CKT 1 | 92 | 108.9607 | 109.1991 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
05SH | WERE | WERE | EXIDE JCT - SUMMIT 115KV | 57381 SUMMIT 3 115 to 57368 EXIDE J3 115 CKT 1 | 196 | 105.4933 | 105.562 | NORTHVIEW - SUMMIT 115KV | 57371 NORTHVW3 115 to 57381 SUMMIT 3 115 CKT 1 | 0 | Rebuild and reconductor 4.94 miles with 1192 ACSR. | 1100000
05SH | WERE | WERE | EXIDE JCT - SUMMIT 115KV | 57381 SUMMIT 3 115 to 57368 EXIDE J3 115 CKT 1 | 196 | 100.9694 | 101.2242 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05SH | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 140.6785 | 140.818 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 123.1479 | 123.2699 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 129.4684 | 129.6097 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 113.0589 | 113.1823 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 131.322 | 131.4619 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 114.7091 | 114.8313 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | TECUMSEH HILL 161/115KV TRANSFORMER | 56920 TECHILL5 161 WND 1 1 | 69 | 100.2422 | 100.3413 | HOYT - HOYT HTI SWITCHING JCT 115KV CKT 1 | 57163 HOYT 3 115 to 57165 HTI JCT3 115 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 632 Overload of the Tecumseh Hill 161/115kV Transformer
05SH | WERE | WERE | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57343 WJCCTYE3 115 to 57342 WJCCTY 3 115 CKT 1 | 141 | 100.8718 | 101.1114 | JEFFREY ENERGY CENTER - SUMMIT 345KV | 56766 JEC N 7 345 to 56773 SUMMIT 7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 402 Outage of the Jeffrey Energy Center to Summit 345 kV Line
05SH | WERE | WERE | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57343 WJCCTYE3 115 to 57342 WJCCTY 3 115 CKT 1 | 141 | 100.6633 | 100.8999 | SUMMIT 345/230KV TRANSFORMER CKT 1 | 56773 SUMMIT 7 345 to 56873 SUMMIT 6 230 to 56813 SUMMIT 114.4 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 617 Outage of the Summit 345/230kV Transformer
05SH | AEPW | AEPW | EAST CENTRAL HENRYETTA - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54049 EC.HEN-4 138 CKT 1 | 105 | 87.8832 | 105.0982 | KELCO - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54057 KELCO 4 138 CKT 1 | 844.6211 | See Previous Upgrade Specified
05SH | AEPW | AEPW | EAST CENTRAL HENRYETTA - WELEETKA 138KV | 54049 EC.HEN-4 138 to 54028 WELETK4 138 CKT 1 | 105 | 84.1328 | 101.3502 | KELCO - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54057 KELCO 4 138 CKT 1 | 1105.8954 | See Previous Upgrade Specified
05SH | SWPA | AECI | DONIPHAN 161/69KV TRANSFORMER CKT 1 | 52640 DONIPHN5 161 to 97201 2DONIPH 69 CKT 1 | 18.75 | 151.5073 | 151.7276 | DONIPHAN 161/69KV TRANSFORMER CKT 2 | 52640 DONIPHN5 161 to 97201 2DONIPH 69 CKT 2 | 1200 | Local area problem. Transformer is owned by AECI.
05SH | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57343 WJCCTYE3 115 to 57328 FT JCT 3 115 CKT 1 | 68 | 104.2758 | 104.4957 | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 1200 | Invalid Contingency
05FA | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57151 AUBURN 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 137.2796 | 137.4624 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57151 AUBURN 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 125.6496 | 125.7685 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57151 AUBURN 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 120.0166 | 120.1765 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 109.8748 | 109.9789 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | GRRD | GRRD | BRISTOW - KELLYVILLE 69KV | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 101.2262 | 101.3505 | MANFORD - SILVER CITY 69KV | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 0 | GRDA to Construct 138/69 KV Fisher Sub, tapping Keystone -- Silver City 138 KV T-line by 6/2005
05FA | EMDE | SWPA | CARTHAGE - SUB 109 - ATLAS JCT. 161KV | 59466 ATL109 5 161 to 52688 CARTHAG5 161 CKT 1 | 167 | 111.9745 | 112.4014 | SUB 292 - TIPTON FORD - SUB 389 - JOPLIN SOUTHWEST 161KV | 59472 TIP292 5 161 to 59483 JOP389 5 161 CKT 1 | 0 | Replace 600 Amp disconnect switches | 60000
05FA | EMDE | SWPA | CARTHAGE - SUB 109 - ATLAS JCT. 161KV | 59466 ATL109 5 161 to 52688 CARTHAG5 161 CKT 1 | 167 | 101.9824 | 102.3466 | SUB 349 - ASBURY - SUB 421 - PURCELL SOUTHWEST 161KV | 59476 ASB349 5 161 to 59491 PUR421 5 161 CKT 1 | 0 | See Previous Upgrade Specified
05FA | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 100.8693 | 101.0665 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05FA | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 100.2498 | 100.4456 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05FA | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 111.8219 | 112.0078 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05FA | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 106.2042 | 106.3986 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05FA | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57301 EAST ST3 115 to 57309 WEMPORI3 115 CKT 1 | 92 | 100.5693 | 100.7924 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
05FA | WERE | WERE | EXIDE JCT - NORTH AMERICAN PHILIPS 115KV | 57368 EXIDE J3 115 to 57372 PHILIPS3 115 CKT 1 | 196 | 102.2528 | 102.4649 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | Rebuild and reconductor 0.34 miles with 1192 ACSR. | 95200
05FA | WERE | WERE | EXIDE JCT - SUMMIT 115KV | 57381 SUMMIT 3 115 to 57368 EXIDE J3 115 CKT 1 | 196 | 107.4521 | 107.6668 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05FA | WERE | WERE | EXIDE JCT - SUMMIT 115KV | 57381 SUMMIT 3 115 to 57368 EXIDE J3 115 CKT 1 | 196 | 101.1912 | 101.2568 | NORTHVIEW - SUMMIT 115KV | 57371 NORTHVW3 115 to 57381 SUMMIT 3 115 CKT 1 | 0 | See Previous Upgrade Specified
05FA | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 | 68 | 100.5271 | 100.7188 | JEFFREY ENERGY CENTER - SUMMIT 345KV | 56766 JEC N 7 345 to 56773 SUMMIT 7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 402 Outage of the Jeffrey Energy Center to Summit 345 kV Line
05FA | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 | 68 | 100.2163 | 100.4048 | SUMMIT 345/230KV TRANSFORMER CKT 1 | 56773 SUMMIT 7 345 to 56873 SUMMIT 6 230 to 56813 SUMMIT 114.4 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 617 Outage of the Summit 345/230kV Transformer
05FA | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 131.5447 | 131.7266 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 119.8256 | 119.9441 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 115.0939 | 115.2532 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 104.8435 | 104.9472 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 104.0997 | 104.2939 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05FA | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 122.3827 | 122.5632 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 110.5472 | 110.6648 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 106.864 | 107.0217 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JCT (SOUTH) 115KV | 57372 PHILIPS3 115 to 57374 SPHILPJ3 115 CKT 1 | 160 | 113.5114 | 113.9525 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05FA | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 122.5213 | 122.9973 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05FA | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 2 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 2 | 92 | 106.9258 | 107.3415 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05FA | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 124.057 | 124.2376 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 112.1545 | 112.2724 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 108.3451 | 108.5029 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | EMDE | EMDE | SUB 110 - ORONOGO JCT. - SUB 432 - JOPLIN OAKLAND NORTH 161KV | 59467 ORO110 5 161 to 59494 OAK432 5 161 CKT 1 | 214 | 101.3483 | 101.6487 | SUB 292 - TIPTON FORD - SUB 389 - JOPLIN SOUTHWEST 161KV | 59472 TIP292 5 161 to 59483 JOP389 5 161 CKT 1 | 0 | Reconstruct and replace 1.4 miles of 556 ACSR with Bundled 556 ACSR. | 800000
05FA | WERE | WERE | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57343 WJCCTYE3 115 to 57342 WJCCTY 3 115 CKT 1 | 141 | 105.8524 | 106.0544 | JEFFREY ENERGY CENTER - SUMMIT 345KV | 56766 JEC N 7 345 to 56773 SUMMIT 7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 402 Outage of the Jeffrey Energy Center to Summit 345 kV Line
05FA | WERE | WERE | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57343 WJCCTYE3 115 to 57342 WJCCTY 3 115 CKT 1 | 141 | 105.5246 | 105.7231 | SUMMIT 345/230KV TRANSFORMER CKT 1 | 56773 SUMMIT 7 345 to 56873 SUMMIT 6 230 to 56813 SUMMIT 114.4 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 617 Outage of the Summit 345/230kV Transformer
05FA | EMDE | SWPA | CARTHAGE - SUB 109 - ATLAS JCT. 161KV | 59466 ATL109 5 161 to 52688 CARTHAG5 161 CKT 1 | 167 | 99.7636 | 100.1565 | SUB 395 - CARTHAGE SOUTHWEST - SUB 421 - PURCELL SOUTHWEST 161KV | 59485 CAR395 5 161 to 59491 PUR421 5 161 CKT 1 | 722.0644 | See Previous Upgrade Specified
05FA | WERE | WERE | EL PASO - GILL ENERGY CENTER SOUTH 138KV | 57039 ELPASO 4 138 to 57046 GILL S 4 138 CKT 1 | 210 | 115.5366 | 115.7261 | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV | 57040 EVANS N4 138 to 57041 EVANS S4 138 CKT 1 | 1200 | Invalid Contingency
05WP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57151 AUBURN 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 110.2832 | 110.408 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05WP | GRRD | GRRD | BRISTOW - KELLYVILLE 69KV | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 100.3131 | 100.4908 | MANFORD - SILVER CITY 69KV | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 0 | GRDA to Construct 138/69 KV Fisher Sub, tapping Keystone -- Silver City 138 KV T-line by 6/2005
05WP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 275 | 103.1067 | 103.6485 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 112.2829 | 112.5299 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05WP | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 108.1486 | 108.4053 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05WP | AEPW | AEPW | JERICHO 115/69KV TRANSFORMER | 54276 JERICHO3 115 WND 2 1 | 46 | 107.2874 | 108.0504 | AMOCO TAP - CHILDRESS 69KV CKT 1 | 54287 AMOCOTP269.0 to 54289 CHLDR2WT69.0 CKT 1 | 0 | Solution Undetermined
05WP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 105.2513 | 105.3816 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05WP | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 106.2104 | 106.4665 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05WP | SWPA | SWPA | NORFORK 161/69KV TRANSFORMER CKT 1 | 52648 NORFORK5 161 WND 2 NFK X1 1 | 25 | 110.3021 | 110.3696 | NORFORK 161/69KV TRANSFORMER CKT 2 | 52648 NORFORK5 161 to 52650 NORFORK269.0 to 52651 NFK X2 113.8 CKT 1 | 0 | See Previous Upgrade Specified
05WP | WERE | WERE | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JCT (SOUTH) 115KV | 57372 PHILIPS3 115 to 57374 SPHILPJ3 115 CKT 1 | 160 | 105.4654 | 106.0118 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 113.8472 | 114.4368 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05WP | WERE | WERE | EL PASO - GILL ENERGY CENTER SOUTH 138KV | 57039 ELPASO 4 138 to 57046 GILL S 4 138 CKT 1 | 210 | 103.3751 | 103.5698 | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV | 57040 EVANS N4 138 to 57041 EVANS S4 138 CKT 1 | 1200 | Invalid Contingency
05WP | AEPW | AEPW | JERICHO 115/69KV TRANSFORMER | 54276 JERICHO3 115 WND 2 1 | 46 | 107.2654 | 108.0255 | CHILDRESS 138/69KV TRANSFORMER CKT 1 | 54289 CHLDR2WT69.0 to 54290 CHILD4WT 138 to 54305 WC2TERT 12.5 CKT 1 | 1200 | Invalid Contingency
07SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 172.1621 | 172.2828 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 155.0746 | 155.289 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 150.5607 | 150.6662 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 135.6328 | 135.8203 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | GRRD | GRRD | BRISTOW - KELLYVILLE 69KV | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 131.201 | 131.495 | MANFORD - SILVER CITY 69KV | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 0 | GRDA to Construct 138/69 KV Fisher Sub, tapping Keystone -- Silver City 138 KV T-line by 6/2005
07SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 113.3566 | 113.6619 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 109.5358 | 109.7997 | SUB 382 - LARUSSEL - SUB 383 - MONETT 161KV | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 108.6758 | 108.9799 | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 103.0938 | 103.3928 | JASPER - LAMAR 69KV | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 102.1919 | 102.4427 | SUB 124 - AURORA H.T. - SUB 355 - AURORA WEST 69KV | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 106.2279 | 106.3605 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
07SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 104.7282 | 104.8619 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
07SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 105.585 | 105.7191 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
07SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52690 CARTHG 269.0 WND 1 CRG X2 1 | 84 | 104.0506 | 104.1858 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
07SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 108.7882 | 108.9479 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 101.1977 | 101.6403 | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 145.8185 | 146.7008 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 133.7874 | 134.3271 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 130.0556 | 130.9475 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 110.1002 | 110.783 | FLINT CREEK - GENTRY REC 161KV | 53139 FLINTCR5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 109.1339 | 109.8175 | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | OMPA | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 54157 COMMTAP4 138 to 56204 OMDUNCN4 138 CKT 1 | 117 | 112.5212 | 113.4122 | CORNVILLE - RUSH SPRINGS NATURAL GAS TAP 138KV | 54112 CORNVIL4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | OMPA | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 54157 COMMTAP4 138 to 56204 OMDUNCN4 138 CKT 1 | 117 | 102.8988 | 103.7937 | RUSH SPRINGS NATURAL GAS TAP - RUSH SPRINGS TAP 138KV | 54154 RUSHSPT4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | DYESS - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53131 DYESS 5 161 CKT 1 | 313 | 113.0345 | 113.1043 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | May Limit Renewal Rights
07SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 103.0368 | 103.1274 | LOWELL - TONTITOWN 161KV | 53144 LOWELL 5 161 to 53170 TONTITN5 161 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 100.5365 | 100.6264 | LOWELL - ROGERS 161KV | 53144 LOWELL 5 161 to 53152 ROGERS 5 161 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57309 WEMPORI3 115 to 57301 EAST ST3 115 CKT 1 | 92 | 105.7015 | 105.82 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
07SP | AEPW | AEPW | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 313 | 100.258 | 100.4351 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | May Limit Renewal Rights
07SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 105.9416 | 106.0327 | LOWELL - TONTITOWN 161KV | 53144 LOWELL 5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 103.4482 | 103.5381 | LOWELL - ROGERS 161KV | 53144 LOWELL 5 161 to 53152 ROGERS 5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 102.2495 | 102.3016 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 162.5449 | 162.6653 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 145.7502 | 145.9771 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 142.2843 | 142.3896 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 127.5545 | 127.7535 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | GRDA | GRDA | KINZIE 138/69KV TRANSFORMER | 54510 KINZEGR4 138 to 54513 KINZEGR2 69 CKT 1 | 56 | 126.2645 | 126.524 | CENTRAL - STILLWATER 69KV | 54453 CENTRL 2 69 to 96845 2STILWTR 69 CKT 1 | 0 | Solution Undetermined
07SP | SPS | SPS | KRESS INTERCHANGE 115/69KV TRANSFORMER CKT 1 | 51316 KRESS3 115 to 51315 KRESS2 69 CKT 1 | 44 | 153.6232 | 153.8493 | KRESS INTERCHANGE 115/69KV TRANSFORMER CKT 2 | 51315 KRESS2 69 to 51316 KRESS3 115 CKT 2 | 0 | May be relieved due to Xcel Energy Transmission Operating Directive for Loss of the Kress 115/69 kV autotransformer
07SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57335 MCDOWEL3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 147.0759 | 147.1964 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 131.236 | 131.4921 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57335 MCDOWEL3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 128.4602 | 128.5655 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 114.6015 | 114.8252 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | AEPW | AEPW | SNYDER - TIPTON & HEADERICK 69KV | 54125 HEADRIK2 69 to 54138 SNYDER-2 69 CKT 1 | 53 | 101.4155 | 101.9272 | HOBART JCT - TAMARAC TAP 138KV | 54126 HOB-JCT4 138 to 54158 TAMARTP4 138 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 149.4517 | 149.5711 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 133.5452 | 133.7872 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 130.6016 | 130.706 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 116.6491 | 116.8605 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | AEPW | AEPW | BLUE CIRCLE - CATOOSA 69KV | 53806 BCIRCLE2 69 to 53811 CATOOSA2 69 CKT 1 | 72 | 104.7563 | 105.0389 | LYNN LANE TAP - LYNN LANE WEST TAP 138KV | 53782 LLAN WT4 138 to 53816 LLANETP4 138 CKT 1 | 1200 | Invalid Contingency
07SP | AEPW | AEPW | MCALESTER - WELEETKA 69KV | 54024 MCALEST2 69 to 54029 WELEETK2 69 CKT 1 | 52 | 134.2412 | 134.4697 | LONE OAK - SOUTH MCALESTER TAP 138KV | 54022 LONEOAK4 138 to 54032 SMCALTP4 138 CKT 1 | 1200 | Invalid Contingency
07WP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 43 | 104.8407 | 105.1985 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07WP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 43 | 100.311 | 100.6438 | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07WP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 275 | 106.2806 | 107.0013 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 108.5235 | 108.6063 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
07WP | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 102.7234 | 102.8089 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
07WP | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 100.5755 | 100.6609 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
07WP | WERE | WERE | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JCT (SOUTH) 115KV | 57372 PHILIPS3 115 to 57374 SPHILPJ3 115 CKT 1 | 160 | 111.2832 | 111.7693 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
07WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 120.1261 | 120.6504 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
07WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 2 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 2 | 92 | 104.8178 | 105.2757 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
07WP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57301 EAST ST3 115 to 57309 WEMPORI3 115 CKT 1 | 92 | 99.9152 | 100.1435 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 445.7293 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
07WP | WERE | WERE | EL PASO - GILL ENERGY CENTER SOUTH 138KV | 57039 ELPASO 4 138 to 57046 GILL S 4 138 CKT 1 | 210 | 105.6178 | 105.877 | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV | 57040 EVANS N4 138 to 57041 EVANS S4 138 CKT 1 | 1200 | Invalid Contingency
10SP | AEPW | AEPW | ANTLERS TAP - VALLEY TIMBER 69KV | 54019 VALYTIM2 69 to 54041 ANTLTAP2 69 CKT 1 | 48 | 101.2238 | 101.6678 | ALLEN NATURAL GAS TAP - TUPELO 138KV | 52800 TUPELO 4 138 to 54006 ALLENGT4 138 CKT 1 | 0 | Possible Invalid Contingency
10SP | AEPW | AEPW | ATOKA 138/69KV TRANSFORMER | 54007 ATOKA--269.0 WND 1 1 | 36 | 105.7499 | 105.8122 | ALLEN NATURAL GAS TAP - TUPELO 138KV | 52800 TUPELO 4 138 to 54006 ALLENGT4 138 CKT 1 | 0 | Possible Invalid Contingency
10SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 221.6486 | 221.7721 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 180.5945 | 180.7728 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 193.8228 | 193.9308 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 157.941 | 158.0969 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | GRRD | GRRD | BRISTOW - KELLYVILLE 69KV | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 145.174 | 145.448 | MANFORD - SILVER CITY 69KV | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 0 | GRDA to Construct 138/69 KV Fisher Sub, tapping Keystone -- Silver City 138 KV T-line by 6/2005
10SP | SWPA | SPRM | BROOKLINE - SPRINGFIELD 161KV | 52692 SPRGFLD5 161 to 59969 BRKLNE 5 161 CKT 1 | 323 | 103.8995 | 103.968 | BROOKLINE - JCT 161KV | 59955 JUNCTN 5 161 to 59969 BRKLNE 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | SWPA | AECI | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 47 | 104.9571 | 105.0661 | 2MILO - 2CLARK 69KV CKT 1 | 96654 2MILO 69 to 96802 2CLARK 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 118.0388 | 118.3603 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 115.0522 | 115.3008 | SUB 382 - LARUSSEL - SUB 383 - MONETT 161KV | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 112.8143 | 113.118 | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 106.8048 | 107.1037 | JASPER - LAMAR 69KV | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 106.286 | 106.5363 | SUB 124 - AURORA H.T. - SUB 355 - AURORA WEST 69KV | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 111.335 | 111.4658 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
10SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 109.9227 | 110.0548 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
10SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 110.6496 | 110.7795 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
10SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52690 CARTHG 269.0 WND 1 CRG X2 1 | 84 | 109.2023 | 109.3335 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
10SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 125.5491 | 125.7128 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 114.4222 | 114.8675 | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 107.5494 | 107.71 | EAST FAYETTEVILLE REC - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53193 EFAYTVL5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 106.9482 | 107.1913 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 105.4135 | 105.7131 | FLINT CREEK - GENTRY REC 161KV | 53139 FLINTCR5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - FLINT CREEK 161KV | 53154 CHAMSPR5 161 to 53139 FLINTCR5 161 CKT 1 | 335 | 107.7744 | 107.8817 | CHAMBER SPRINGS 345/161KV TRANSFORMER | 53154 CHAMSPR5 161 to 53155 CHAMSPR7 345 to 53120 CHAMSPR113.8 CKT 1 | 0 | May Limit Renewal Rights
10SP | AEPW | AEPW | CHAMBER SPRINGS - FLINT CREEK 161KV | 53154 CHAMSPR5 161 to 53139 FLINTCR5 161 CKT 1 | 335 | 107.7731 | 107.8804 | CHAMBER SPRINGS - CLARKSVILLE 345KV | 53155 CHAMSPR7 345 to 53756 CLARKSV7 345 CKT 1 | 0 | May Limit Renewal Rights
10SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 166.2418 | 167.1591 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 149.8959 | 150.4372 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 146.4557 | 147.3785 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 123.5333 | 124.2378 | FLINT CREEK - GENTRY REC 161KV | 53139 FLINTCR5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 122.1862 | 122.8912 | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | WERE | WERE | CHASE - WHITE JCT 69KV | 57605 WHITE J269.0 to 57588 CHASE 269.0 CKT 1 | 43 | 103.2658 | 103.423 | WEAVER 138/69KV TRANSFORMER CKT 1 | 56991 WEAVER 4 138 to 57604 WEAVER 269.0 to 57083 WEAVER 113.2 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 634 Outage of the Weaver 138-69kV Transformer
10SP | OMPA | AEPW | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 56204 OMDUNCN4 138 to 54157 COMMTAP4 138 CKT 1 | 117 | 121.1464 | 122.0974 | CORNVILLE - RUSH SPRINGS NATURAL GAS TAP 138KV | 54112 CORNVIL4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | OMPA | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 54157 COMMTAP4 138 to 56204 OMDUNCN4 138 CKT 1 | 117 | 111.239 | 112.1951 | RUSH SPRINGS NATURAL GAS TAP - RUSH SPRINGS TAP 138KV | 54154 RUSHSPT4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | OMPA | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 54157 COMMTAP4 138 to 56204 OMDUNCN4 138 CKT 1 | 117 | 106.9198 | 107.8732 | OMPA-MARLOW - RUSH SPRINGS TAP 138KV | 54154 RUSHSPT4 138 to 56207 OMMARLO4 138 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | DYESS - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53131 DYESS 5 161 CKT 1 | 313 | 133.192 | 133.3043 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | AEPW | AEPW | DYESS - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53131 DYESS 5 161 CKT 1 | 313 | 107.9919 | 108.0884 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 111.3118 | 111.4 | LOWELL - TONTITOWN 161KV | 53144 LOWELL 5 161 to 53170 TONTITN5 161 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 109.4136 | 109.4871 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 108.3885 | 108.4758 | LOWELL - ROGERS 161KV | 53144 LOWELL 5 161 to 53152 ROGERS 5 161 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 105.8058 | 105.886 | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 105.4272 | 105.4947 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | AEPW | AEPW | EAST FAYETTEVILLE REC - SOUTH SPRINGDALE 161KV | 53193 EFAYTVL5 161 to 53159 SOSPRDL5 161 CKT 1 | 313 | 109.4348 | 109.5348 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57309 WEMPORI3 115 to 57301 EAST ST3 115 CKT 1 | 92 | 118.035 | 118.1623 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
10SP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57309 WEMPORI3 115 to 57301 EAST ST3 115 CKT 1 | 92 | 103.7738 | 103.8985 | MORRIS COUNTY - WEST EMPORIA 115KV | 57305 MORRIS 3 115 to 57309 WEMPORI3 115 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1209 Outage of the Morris-West Emporia 115kV Line
10SP | AEPW | AEPW | ELM SPRINGS REC - TONTITOWN 161KV | 53194 ELMSPRR5 161 to 53170 TONTITN5 161 CKT 1 | 335 | 109.9897 | 110.1442 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | ENTR | AEPW | EUREKA SPRINGS - OSAGE CREEK (AECC) 161KV | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 107.4938 | 107.7117 | BULL SHOALS - BULL SHOALS HES 161KV | 52660 BULL SH5 161 to 99802 5BULLSH* 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | ENTR | AEPW | EUREKA SPRINGS - OSAGE CREEK (AECC) 161KV | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 106.1452 | 106.3641 | BULL SHOALS HES - FLIPPIN 161KV | 99802 5BULLSH* 161 to 99809 5FLIPN 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | ENTR | AEPW | EUREKA SPRINGS - OSAGE CREEK (AECC) 161KV | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 103.0871 | 103.3088 | FLIPPIN - SUMMIT 161KV | 99809 5FLIPN 161 to 99837 5SUMMIT 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | ENTR | AEPW | EUREKA SPRINGS - OSAGE CREEK (AECC) 161KV | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 100.34 | 100.5585 | BEE BRANCH (AECC) - QUITMAN 161KV | 99519 5QUITMN 161 to 99799 5BEE BR 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | AEPW | AEPW | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 313 | 115.8139 | 115.9937 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | AEPW | AEPW | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53195 FARMGTN5 161 to 53157 SFAYTVL5 161 CKT 1 | 313 | 104.2903 | 104.7914 | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 114.7029 | 114.7905 | LOWELL - TONTITOWN 161KV | 53144 LOWELL 5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 112.8072 | 112.8824 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 111.783 | 111.8702 | LOWELL - ROGERS 161KV | 53144 LOWELL 5 161 to 53152 ROGERS 5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 109.1909 | 109.271 | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 108.8059 | 108.8743 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | FLINT CREEK - TONTITOWN 161KV | 53170 TONTITN5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 117.0245 | 117.1479 | CHAMBER SPRINGS 345/161KV TRANSFORMER | 53154 CHAMSPR5 161 to 53155 CHAMSPR7 345 to 53120 CHAMSPR113.8 CKT 1 | 0 | May Limit Renewal Rights
10SP | AEPW | AEPW | FLINT CREEK - TONTITOWN 161KV | 53170 TONTITN5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 117.023 | 117.1462 | CHAMBER SPRINGS - CLARKSVILLE 345KV | 53155 CHAMSPR7 345 to 53756 CLARKSV7 345 CKT 1 | 0 | May Limit Renewal Rights
10SP | WERE | WERE | GRANT JCT - MAHANNA 69KV | 57738 MAHANNA2 69 to 57800 GRANT J2 69 CKT 1 | 101 | 149.8251 | 149.903 | EVANS ENERGY CENTER NORTH - SEDGWICK COUNTY NO. 12 COLWICH 138KV | 57040 EVANS N4 138 to 57065 SG12COL4 138 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1105 Outage of the Moundridge to Halstead 138 kV line, Gordon Evans to Halstead 138 kV line or loss of the Halstead 138 kV bus.
10SP | WERE | WERE | GRANT JCT - RIPLEY 69KV | 57800 GRANT J2 69 to 57832 RIPLEYM2 69 CKT 1 | 108 | 158.3037 | 158.3769 | EVANS ENERGY CENTER NORTH - SEDGWICK COUNTY NO. 12 COLWICH 138KV | 57040 EVANS N4 138 to 57065 SG12COL4 138 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1105 Outage of the Moundridge to Halstead 138 kV line, Gordon Evans to Halstead 138 kV line or loss of the Halstead 138 kV bus.
10SP | AEPW | AEPW | HUGO - VALLEY TIMBER 69KV | 54018 HUGO---2 69 to 54019 VALYTIM2 69 CKT 1 | 48 | 101.3049 | 101.7476 | ALLEN NATURAL GAS TAP - TUPELO 138KV | 52800 TUPELO 4 138 to 54006 ALLENGT4 138 CKT 1 | 0 | Possible Invalid Contingency
10SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 210.3921 | 210.5237 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 169.7796 | 169.956 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 184.1499 | 184.2651 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 148.6245 | 148.7789 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | WERE | WERE | KELLY - SOUTH SENECA 115KV | 57217 KELLY 3 115 to 57337 SENECA 3 115 CKT 1 | 92 | 100.162 | 100.2668 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | GRDA | GRDA | KINZIE 138/69KV TRANSFORMER | 54513 KINZEGR2 69 to 54510 KINZEGR4 138 CKT 1 | 56 | 132.6152 | 132.8201 | CENTRAL - STILLWATER 69KV | 54453 CENTRL 2 69 to 96845 2STILWTR 69 CKT 1 | 0 | Solution Undetermined
10SP | SPS | SPS | LUBBOCK EAST INTERCHANGE 230/115KV TRANSFORMER | 51689 LUBE6 230 to 51688 LUBE3 115 CKT 1 | 172.5 | 113.7052 | 113.7982 | LUBBOCK SOUTH INTERCHANGE 230/115KV TRANSFORMER | 51680 LUBS3 115 to 51681 LUBS6 230 CKT 1 | 0 | May be relieved due to Xcel Energy Transmission Operating Directive for Loss of the 230/115 kV autotransformer at Lubbock South
10SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57335 MCDOWEL3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 191.4692 | 191.6258 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 153.1163 | 153.289 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57335 MCDOWEL3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 167.2275 | 167.3642 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 133.7145 | 133.8653 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | ENTR | AEPW | MURFREESBORO - SOUTH NASHVILLE 138KV | 99389 4MURFRE 138 to 53321 SNASHVL4 138 CKT 1 | 118 | 102.0119 | 102.0735 | 3BISMRK - HOT SPRINGS WEST BUS 115KV | 99397 3BISMRK 115 to 99403 3HSEHVW 115 CKT 1 | 0 | May Limit Renewal Rights
10SP | AEPW | AEPW | PATTERSON - SOUTH NASHVILLE 138KV | 53321 SNASHVL4 138 to 53306 PATTERS4 138 CKT 1 | 118 | 122.4193 | 122.4841 | 3BISMRK - HOT SPRINGS WEST BUS 115KV | 99397 3BISMRK 115 to 99403 3HSEHVW 115 CKT 1 | 0 | May Limit Rollover Rights
10SP | AEPW | AEPW | SNYDER - TIPTON & HEADERICK 69KV | 54125 HEADRIK2 69 to 54138 SNYDER-2 69 CKT 1 | 53 | 113.876 | 114.5319 | HOBART JCT - TAMARAC TAP 138KV | 54126 HOB-JCT4 138 to 54158 TAMARTP4 138 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 194.5169 | 194.6618 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 155.6556 | 155.829 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 169.9649 | 170.0916 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 135.9833 | 136.1346 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | EMDE | EMDE | SUB 383 - MONETT 161/69KV TRANSFORMER | 59480 MON383 5 161 WND 1 MONETT 1 | 150 | 102.4721 | 102.5542 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV CKT 1 | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | GRDA | GRDA | COLLINSVILLE 161/69KV TRANSFORMER CKT 1 | 54427 COLINS 5 161 to 54476 COLNSGR2 69 CKT 1 | 50 | 99.8062 | 100.2877 | COLLINSVILLE 161/69KV TRANSFORMER CKT 2 | 54427 COLINS 5 161 to 54476 COLNSGR2 69 CKT 2 | 483.0055 | May Limit Renewal Rights
10SP | ENTR | AEPW | EUREKA SPRINGS - OSAGE CREEK (AECC) 161KV | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 99.7778 | 100.0009 | HARRISON-EAST - SUMMIT 161KV | 99811 5HARR-E 161 to 99837 5SUMMIT 161 CKT 1 | 1195.1583 | May Limit Renewal Rights
10SP | AEPW | AEPW | BLUE CIRCLE - CATOOSA 69KV | 53806 BCIRCLE2 69 to 53811 CATOOSA2 69 CKT 1 | 72 | 110.1457 | 110.4323 | LYNN LANE TAP - LYNN LANE WEST TAP 138KV | 53782 LLAN WT4 138 to 53816 LLANETP4 138 CKT 1 | 1200 | Invalid Contingency
10SP | AEPW | AEPW | MCALESTER - WELEETKA 69KV | 54024 MCALEST2 69 to 54029 WELEETK2 69 CKT 1 | 52 | 141.5609 | 141.6889 | LONE OAK - SOUTH MCALESTER TAP 138KV | 54022 LONEOAK4 138 to 54032 SMCALTP4 138 CKT 1 | 1200 | Invalid Contingency
10WP | WERE | WERE | 166TH STREET - JARBALO JCT SWITCHING STATION 115KV | 57244 JARBALO3 115 to 57233 166TH 3 115 CKT 1 | 97 | 103.0931 | 103.154 | MIDLAND JCT - PENTAGON 115KV | 57252 MIDLAND3 115 to 57261 PENTAGN3 115 CKT 1 | 0 | May Limit Rollover Rights
10WP | WERE | WERE | ANZIO - FORT JCT SWITCHING STATION 115KV | 57321 ANZIO 3 115 to 57328 FT JCT 3 115 CKT 1 | 92 | 101.5493 | 101.6125 | Multiple Outage Contingency: FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | Multiple Outage Contingency: 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 0 | May be relieved due to Westar Transmission Operating Directive 1217 Outage of the Fort JCT-West JCT City 115kV Line
10WP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 275 | 120.0148 | 120.8552 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10WP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 275 | 110.7074 | 111.1905 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10WP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 275 | 106.1505 | 106.9979 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 114.1283 | 114.3855 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
10WP | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 107.7627 | 108.0232 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
10WP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57301 EAST ST3 115 to 57309 WEMPORI3 115 CKT 1 | 92 | 107.2281 | 107.4065 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
10WP | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 105.5618 | 105.8206 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
10WP | SWPA | SWPA | NORFORK 161/69KV TRANSFORMER CKT 2 | 52650 NORFORK269.0 WND 1 NFK X2 1 | 25 | 100.3461 | 100.8602 | NORFORK 161/69KV TRANSFORMER CKT 1 | 52648 NORFORK5 161 to 52650 NORFORK269.0 to 52649 NFK X1 113.8 CKT 1 | 0 | See Previous Upgrade Specified
10WP | WERE | WERE | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JCT (SOUTH) 115KV | 57372 PHILIPS3 115 to 57374 SPHILPJ3 115 CKT 1 | 160 | 124.4968 | 124.7493 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
10WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 134.379 | 134.6514 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
10WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 2 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 2 | 92 | 117.2635 | 117.5015 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
10WP | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 | 68 | 105.3721 | 105.4545 | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 1200 | Invalid Contingency
[11 empty] | Total Estimated Cost | 43722400

## Table 2
Study Case | From Area | To Area | Monitored Branch Over 100% Rate B | Rate <MVA> | BC % Loading | TC % Loading | Outaged Branch Causing Overload | Comment
04G | MIPU | AECI | 59216 BUTLER_5 161 to 96689 2BUTLER 69 CKT 1 | 56 | 99.6188 | 100.3485 | 59208 NEVADA 5 161 to 59216 BUTLER_5 161 CKT 1
04G | MIPU | MIPU | 59288 RGAFB 2 69 to 59284 GRDVWTP2 69 CKT 1 | 53 | 110.3588 | 110.5204 | 59225 PHILL 5 161 to 59280 PHILL 2 69 CKT 1
04G | MIPU | MIPU | 59289 BELTON 2 69 to 59288 RGAFB 2 69 CKT 1 | 53 | 104.9332 | 105.0939 | 59225 PHILL 5 161 to 59280 PHILL 2 69 CKT 1
04G | MEC | MEC | 63801 CBLUFFS5 161 to 63823 AVOCA 5 161 CKT 1 | 167 | 108.6925 | 108.833 | 63800 CBLUFFS3 345 to 64056 MADISON3 345 CKT 1
04G | OPPD | OPPD | 65390 S1263T1T 161 to 65627 W BROCK8 69 CKT 1 | 53 | 100.6198 | 100.7053 | 64863 HUMBOLT5 161 to 65391 S975T4 T 161 CKT 1
04G | OPPD | OPPD | 65390 S1263T1T 161 to 65627 W BROCK8 69 CKT 1 | 53 | 100.6135 | 100.699 | 65391 S975T4 T 161 to 65575 S975 8 69 CKT 1
04G | OPPD | OPPD | 65463 S1263 5 161 to 65390 S1263T1T 161 CKT 1 | 53 | 103.1632 | 103.2569 | 64863 HUMBOLT5 161 to 65391 S975T4 T 161 CKT 1
04G | OPPD | OPPD | 65463 S1263 5 161 to 65390 S1263T1T 161 CKT 1 | 53 | 103.1599 | 103.2536 | 65391 S975T4 T 161 to 65575 S975 8 69 CKT 1
04SP | AECI | AECI | 96095 5MANSFD 161 WND 2 MANSFLD1 1 | 56 | 105.9063 | 105.983 | 96095 5MANSFD 161 to 97168 2MANSFL 69.0 to 97169 1MNSFLD2 CKT 2
04SP | SWPA | ENTR | 52660 BULL SH5 161 to 99825 5MIDWAY# 161 CKT 1 | 162 | 102.0335 | 102.2531 | 99817 5ISES 1 161 to 99826 5MORFLD 161 CKT 1
04SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 112.2195 | 112.601 | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1
04SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 109.6978 | 110.0692 | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1
04SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 106.0875 | 106.4427 | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1
04SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 104.415 | 104.7802 | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1
04SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 101.9049 | 102.2296 | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1
04SP | NPPD | NPPD | 64953 SCHUYLR7 115 to 64954 SCHUYLR9 34.5 CKT 2 | 35 | 101.1201 | 101.3941 | 64953 SCHUYLR7 115 to 64954 SCHUYLR9 34.5 CKT 1
04SP | AECI | AECI | 96751 2REEDS 69 to 96659 2BOWRML 69 CKT 1 | 36 | 105.7123 | 106.0947 | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1
04SP | AECI | AECI | 96751 2REEDS 69 to 96659 2BOWRML 69 CKT 1 | 36 | 103.2815 | 103.6544 | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1
04SP | AECI | AECI | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 119.7607 | 120.4708 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
04SP | AECI | AECI | 96920 2ALPINE 69 to 96901 2KELYVIL 69 CKT 1 | 51 | 101.1865 | 101.9449 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
04SP | AECI | AECI | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 51 | 103.4645 | 104.0978 | 96889 2BRISTOW 69 to 96901 2KELYVIL 69 CKT 1
04SP | AECI | AECI | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 51 | 99.1689 | 101.6474 | 96137 4BRISTOW 138 to 96140 4SILVCTY 138 CKT 1
04SP | AECI | AECI | 96984 2TENKILR 69 to 96879 2VIAN 69 CKT 1 | 36 | 100.33 | 100.466 | 54447 TAHLQH 2 69 to 96961 2PARK 69 CKT 1
04SH | SWPA | SWPA | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 105.9603 | 106.2001 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
04SH | SWPA | SWPA | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 103.5084 | 103.748 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
04SH | MEC | MEC | 64220 WRIGHT 5 161 to 64201 WEBSTER5 161 CKT 1 | 216 | 107.4188 | 107.4703 | 63719 HOPE 5 161 to 64648 HOPE MD8 69 CKT 1
04SH | MEC | MEC | 64602 AVO MID8 69 to 63823 AVOCA 5 161 CKT 2 | 50 | 107.9499 | 108.0032 | 63823 AVOCA 5 161 to 64603 AVOCMID8 69 CKT 1
04SH | NPPD | NPPD | 64755 BROKENB7 115 to 64756 BROKENBG 69 CKT 2 | 35 | 175.7174 | 175.8417 | 64755 BROKENB7 115 to 64756 BROKENBG 69 CKT 1
04SH | AECI | AECI | 96126 5MOBTAP 161 to 96120 5THMHIL 161 CKT 1 | 372 | 102.2258 | 102.3809 | 96044 7MCCRED 345 to 96049 7THOMHL 345 CKT 1
04FA | IP | MEC | 32415 GALESBRG 138 to 64411 GALESBR5 161 CKT 1 | 100 | 115.6894 | 115.9953 | 64411 GALESBR5 161 to 32415 GALESBRG 138 CKT 2
04FA | IP | MEC | 32415 GALESBRG 138 to 64411 GALESBR5 161 CKT 2 | 100 | 116.9329 | 117.2422 | 64411 GALESBR5 161 to 32415 GALESBRG 138 CKT 1
04WP | AECI | AECI | 96095 5MANSFD 161 WND 2 MANSFLD1 1 | 56 | 107.7718 | 107.9162 | 96095 5MANSFD 161 to 97168 2MANSFL 69.0 to 97169 1MNSFLD2 CKT 2
04WP | AECI | AECI | 96095 5MANSFD 161 WND 2 MANSFLD2 2 | 56 | 108.0396 | 108.1845 | 96095 5MANSFD 161 to 97168 2MANSFL 69.0 to 97170 1MNSFLD1 CKT 1
04WP | IP | MEC | 32415 GALESBRG 138 to 64411 GALESBR5 161 CKT 1 | 100 | 105.7348 | 105.9254 | 64411 GALESBR5 161 to 32415 GALESBRG 138 CKT 2
04WP | IP | MEC | 32415 GALESBRG 138 to 64411 GALESBR5 161 CKT 2 | 100 | 107.0413 | 107.2342 | 64411 GALESBR5 161 to 32415 GALESBRG 138 CKT 1
04WP | OPPD | OPPD | 65390 S1263T1T 161 to 65627 W BROCK8 69 CKT 1 | 53 | 114.0933 | 114.1866 | 64863 HUMBOLT5 161 to 65391 S975T4 T 161 CKT 1
04WP | OPPD | OPPD | 65390 S1263T1T 161 to 65627 W BROCK8 69 CKT 1 | 53 | 114.0867 | 114.1799 | 65391 S975T4 T 161 to 65575 S975 8 69 CKT 1
04WP | OPPD | OPPD | 65463 S1263 5 161 to 65390 S1263T1T 161 CKT 1 | 53 | 117.2443 | 117.341 | 64863 HUMBOLT5 161 to 65391 S975T4 T 161 CKT 1
04WP | OPPD | OPPD | 65463 S1263 5 161 to 65390 S1263T1T 161 CKT 1 | 53 | 117.2406 | 117.3373 | 65391 S975T4 T 161 to 65575 S975 8 69 CKT 1
05AP | AEPW | CELE | 53461 WALLAKE4 138 to 50090 IPAPER 4 138 CKT 1 | 236 | 100.2983 | 101.6457 | 50045 DOLHILL7 345 to 50046 DOLHILL6 230 CKT 1 | May be relieved by Dolet Hills Operating Guide
05G |  |  | NONE IDENTIFIED
05SP | SWPA | SWPA | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 101.2727 | 101.4264 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
05SP | SWPA | SWPA | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 100.2918 | 100.4466 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
05SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 112.7228 | 113.0773 | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1
05SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 108.9382 | 109.2865 | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1
05SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 107.3321 | 107.6239 | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1
05SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 103.6568 | 104.0031 | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1
05SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 101.9003 | 102.1912 | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1
05SP | AECI | AECI | 96751 2REEDS 69 to 96659 2BOWRML 69 CKT 1 | 36 | 105.9936 | 106.349 | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1
05SP | AECI | AECI | 96751 2REEDS 69 to 96659 2BOWRML 69 CKT 1 | 36 | 102.2681 | 102.6179 | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1
05SP | AECI | AECI | 96751 2REEDS 69 to 96659 2BOWRML 69 CKT 1 | 36 | 100.51 | 100.8031 | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1
05SP | AECI | AECI | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 51 | 104.39 | 104.7628 | 96889 2BRISTOW 69 to 96901 2KELYVIL 69 CKT 1
05SP | AECI | AECI | 96984 2TENKILR 69 to 96879 2VIAN 69 CKT 1 | 36 | 103.2246 | 103.2807 | 54447 TAHLQH 2 69 to 96961 2PARK 69 CKT 1
05SH | SWPA | SWPA | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 110.4321 | 110.6621 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
05SH | SWPA | SWPA | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 109.7852 | 110.0135 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
05SH | SWPA | SWPA | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 107.4866 | 107.7143 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
05SH | SWPA | SWPA | 52690 CARTHG 269.0 WND 1 CRG X2 1 | 84 | 106.6756 | 106.9012 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
05SH | SWPA | AECI | 52640 DONIPHN5 161 to 97201 2DONIPH 69 CKT 1 | 18.75 | 151.5073 | 151.7276 | 52640 DONIPHN5 161 to 97201 2DONIPH 69 CKT 2
05SH | MEC | MEC | 64220 WRIGHT 5 161 to 64201 WEBSTER5 161 CKT 1 | 216 | 104.3386 | 104.393 | 63719 HOPE 5 161 to 64648 HOPE MD8 69 CKT 1
05SH | OPPD | OPPD | 65463 S1263 5 161 to 65390 S1263T1T 161 CKT 1 | 53 | 100.2983 | 100.4005 | 64863 HUMBOLT5 161 to 65391 S975T4 T 161 CKT 1
05SH | OPPD | OPPD | 65463 S1263 5 161 to 65390 S1263T1T 161 CKT 1 | 53 | 100.294 | 100.3961 | 65391 S975T4 T 161 to 65575 S975 8 69 CKT 1
05SH | AECI | AECI | 96120 5THMHIL 161 96126 5MOBTAP 161 1 | 372 | 102.4178 | 102.4981 | Multiple Outage Contingency: 96049 7THOMHL 345 to 96044 7MCCRED 345 CKT 1 96044 7MCCRED 345 to 96043 7KINGDM 345 CKT 1
05FA | SWPA | SWPA | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 100.8693 | 101.0665 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
05FA | SWPA | SWPA | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 100.2498 | 100.4456 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
05FA | AECI | AECI | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 101.2262 | 101.3505 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
05WP | OPPD | OPPD | 65390 S1263T1T 161 to 65627 W BROCK8 69 CKT 1 | 53 | 113.5843 | 113.764 | 64863 HUMBOLT5 161 to 65391 S975T4 T 161 CKT 1
05WP | OPPD | OPPD | 65390 S1263T1T 161 to 65627 W BROCK8 69 CKT 1 | 53 | 113.575 | 113.7547 | 65391 S975T4 T 161 to 65575 S975 8 69 CKT 1
05WP | OPPD | OPPD | 65463 S1263 5 161 to 65390 S1263T1T 161 CKT 1 | 53 | 116.8556 | 117.0377 | 64863 HUMBOLT5 161 to 65391 S975T4 T 161 CKT 1
05WP | OPPD | OPPD | 65463 S1263 5 161 to 65390 S1263T1T 161 CKT 1 | 53 | 116.8507 | 117.0328 | 65391 S975T4 T 161 to 65575 S975 8 69 CKT 1
05WP | AECI | AECI | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 100.3131 | 100.4908 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
07SP | SWPA | SWPA | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 106.2279 | 106.3605 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
07SP | SWPA | SWPA | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 105.585 | 105.7191 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
07SP | SWPA | SWPA | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 104.7282 | 104.8619 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
07SP | SWPA | SWPA | 52690 CARTHG 269.0 WND 1 CRG X2 1 | 84 | 104.0506 | 104.1858 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
07SP | AECI | AECI | 96124 5HOLDEN 161 WND 2 HOLDEN 1 | 56 | 118.2981 | 118.369 | 96110 5PITTSV 161 to 96124 5HOLDEN 161 CKT 1
07SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 113.3566 | 113.6619 | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1
07SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 109.5358 | 109.7997 | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1
07SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 108.6758 | 108.9799 | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1
07SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 103.0938 | 103.3928 | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1
07SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 102.1919 | 102.4427 | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1
07SP | NPPD | NPPD | 64860 HOSKINS7 115 to 64918 NORFK.N7 115 CKT 1 | 132 | 101.3349 | 101.385 | 64860 HOSKINS7 115 to 64920 NORFOLK7 115 CKT 1
07SP | AECI | AECI | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1 | 36 | 101.712 | 101.844 | 96654 2MILO 69 to 96802 2CLARK 69 CKT 1
07SP | AECI | AECI | 96751 2REEDS 69 to 96659 2BOWRML 69 CKT 1 | 36 | 106.1828 | 106.4893 | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1
07SP | AECI | AECI | 96751 2REEDS 69 to 96659 2BOWRML 69 CKT 1 | 36 | 102.296 | 102.559 | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1
07SP | AECI | AECI | 96751 2REEDS 69 to 96659 2BOWRML 69 CKT 1 | 36 | 101.5549 | 101.8612 | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1
07SP | AECI | AECI | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 131.201 | 131.495 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
07SP | AECI | AECI | 96920 2ALPINE 69 to 96901 2KELYVIL 69 CKT 1 | 51 | 110.8805 | 111.3001 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
07SP | AECI | AECI | 96931 2FISHER 69 to 96920 2ALPINE 69 CKT 1 | 51 | 99.9855 | 100.3752 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
07SP | AECI | AECI | 96936 2MANFORD 69 to 96931 2FISHER 69 CKT 1 | 36 | 106.4243 | 106.8615 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
07SP | AECI | AECI | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 51 | 109.5303 | 109.6366 | 96889 2BRISTOW 69 to 96901 2KELYVIL 69 CKT 1
07WP | AECI | AECI | 96081 5GAINES 161 WND 2 GAINESVL 1 | 56 | 100.5593 | 100.661 | 52648 NORFORK5 161 to 96123 5WPLAIN 161 to 52615 PRG X3 113.8 CKT 1
07WP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 43 | 104.8407 | 105.1985 | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1
07WP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 43 | 100.311 | 100.6438 | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1
07WP | OPPD | OPPD | 65463 S1263 5 161 to 65390 S1263T1T 161 CKT 1 | 53 | 115.349 | 115.4013 | 65391 S975T4 T 161 to 65575 S975 8 69 CKT 1
10SP | SWPA | SWPA | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 111.335 | 111.4658 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
10SP | SWPA | SWPA | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 110.6496 | 110.7795 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
10SP | SWPA | SWPA | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 109.9227 | 110.0548 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
10SP | SWPA | SWPA | 52690 CARTHG 269.0 WND 1 CRG X2 1 | 84 | 109.2023 | 109.3335 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | Transformer owned by City of Carthage and AECI.
10SP | AECI | AECI | 96124 5HOLDEN 161 WND 2 HOLDEN 1 | 56 | 126.243 | 126.3168 | 96110 5PITTSV 161 to 96124 5HOLDEN 161 CKT 1
10SP | SWPA | AECI | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 47 | 104.9571 | 105.0661 | 96654 2MILO 69 to 96802 2CLARK 69 CKT 1
10SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 118.0388 | 118.3603 | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1
10SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 115.0522 | 115.3008 | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1
10SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 112.8143 | 113.118 | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1
10SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 106.8048 | 107.1037 | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1
10SP | SWPA | AECI | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 106.286 | 106.5363 | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1
10SP | SWPA | SPRM | 52692 SPRGFLD5 161 to 59969 BRKLNE 5 161 CKT 1 | 323 | 103.8995 | 103.968 | 59955 JUNCTN 5 161 to 59969 BRKLNE 5 161 CKT 1 | Third Party Line Owned by AECI
10SP | NPPD | NPPD | 64860 HOSKINS7 115 to 64918 NORFK.N7 115 CKT 1 | 132 | 104.3095 | 104.3622 | 64860 HOSKINS7 115 to 64920 NORFOLK7 115 CKT 1
10SP | NPPD | NPPD | 64860 HOSKINS7 115 to 64920 NORFOLK7 115 CKT 1 | 132 | 102.301 | 102.3527 | 64860 HOSKINS7 115 to 64918 NORFK.N7 115 CKT 1
10SP | AECI | AECI | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1 | 36 | 108.1625 | 108.2967 | 96654 2MILO 69 to 96802 2CLARK 69 CKT 1
10SP | AECI | AECI | 96751 2REEDS 69 to 96659 2BOWRML 69 CKT 1 | 36 | 110.4533 | 110.7748 | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1
10SP | AECI | AECI | 96751 2REEDS 69 to 96659 2BOWRML 69 CKT 1 | 36 | 107.4272 | 107.6772 | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1
10SP | AECI | AECI | 96751 2REEDS 69 to 96659 2BOWRML 69 CKT 1 | 36 | 105.2641 | 105.5699 | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1
10SP | AECI | AECI | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 145.174 | 145.448 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
10SP | AECI | AECI | 96920 2ALPINE 69 to 96901 2KELYVIL 69 CKT 1 | 51 | 123.6805 | 124.0707 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
10SP | AECI | AECI | 96931 2FISHER 69 to 96920 2ALPINE 69 CKT 1 | 51 | 111.4661 | 111.8239 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
10SP | AECI | AECI | 96936 2MANFORD 69 to 96931 2FISHER 69 CKT 1 | 36 | 118.2044 | 118.5948 | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1
10SP | AECI | AECI | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 51 | 115.4004 | 115.705 | 96889 2BRISTOW 69 to 96901 2KELYVIL 69 CKT 1
10SP | AECI | AECI | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 51 | 99.5473 | 101.5317 | 96137 4BRISTOW 138 to 96140 4SILVCTY 138 CKT 1
10SP | AECI | AECI | 96984 2TENKILR 69 to 96879 2VIAN 69 CKT 1 | 36 | 117.743 | 117.8006 | 54447 TAHLQH 2 69 to 96961 2PARK 69 CKT 1
10SP | ENTR | AEPW | 99389 4MURFRE 138 to 53321 SNASHVL4 138 CKT 1 | 118 | 102.0119 | 102.0735 | 99397 3BISMRK 115 to 99403 3HSEHVW 115 CKT 1
10SP | ENTR | AEPW | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 107.4938 | 107.7117 | 52660 BULL SH5 161 to 99802 5BULLSH* 161 CKT 1
10SP | ENTR | AEPW | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 106.1452 | 106.3641 | 99802 5BULLSH* 161 to 99809 5FLIPN 161 CKT 1
10SP | ENTR | AEPW | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 103.0871 | 103.3088 | 99809 5FLIPN 161 to 99837 5SUMMIT 161 CKT 1
10SP | ENTR | AEPW | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 100.34 | 100.5585 | 99519 5QUITMN 161 to 99799 5BEE BR 161 CKT 1
10WP | AECI | AECI | 96082 5GEORGE 161 WND 2 GRGTWN1 1 | 56 | 101.5748 | 101.6688 | 96105 5NORTON 161 to 96540 2NORTON 69.0 to 96539 1NORTON CKT 1
10WP | AECI | AECI | 96095 5MANSFD 161 WND 2 MANSFLD2 2 | 56 | 109.225 | 109.2986 | 96095 5MANSFD 161 to 97168 2MANSFL 69.0 to 97170 1MNSFLD1 CKT 1
10WP | AECI | AECI | 96108 5OSCEOL 161 WND 2 OSCEOLA 1 | 56 | 110.0267 | 110.2018 | 96692 2CLINTN 69.0 to 96701 2GAINES 69.0 CKT 1
10WP | AECI | AECI | 96108 5OSCEOL 161 WND 2 OSCEOLA 1 | 56 | 100.8735 | 101.052 | 96701 2GAINES 69.0 to 96810 2MTZION 69.0 CKT 1
10WP | AECI | AECI | 96108 5OSCEOL 161 WND 2 OSCEOLA 1 | 56 | 100.0209 | 100.1839 | 52698 STOCKT N5 161 to 96108 5OSCEOL 161 to 52697 NXA X1 113.8 CKT 1
10WP | AECI | AECI | 96692 2CLINTN 69.0 to 96701 2GAINES 69.0 CKT 1 | 43 | 106.8307 | 107.0273 | 96108 5OSCEOL 161 to 96811 2OSCEOL 69.0 to 96812 1OSCEOLA CKT 1
10WP | AECI | AECI | 96811 2OSCEOL 69.0 WND 1 OSCEOLA 1 | 56 | 109.0379 | 109.2156 | 96692 2CLINTN 69.0 to 96701 2GAINES 69.0 CKT 1
10WP | AECI | AECI | 96811 2OSCEOL 69.0 WND 1 OSCEOLA 1 | 56 | 100.7886 | 100.9707 | 96701 2GAINES 69.0 to 96810 2MTZION 69.0 CKT 1
10WP | AMRN | AMRN | 31408 OVERTON 345 to 31409 OVERTON 161 CKT 1 | 300 | 112.5389 | 112.6199 | 96043 7KINGDM 345 to 96090 5KINGDM 161 CKT 1
10WP | AMRN | AMRN | 31408 OVERTON 345 to 31409 OVERTON 161 CKT 1 | 300 | 112.4864 | 112.5675 | 96043 7KINGDM 345 to 96044 7MCCRED 345 CKT 1
10WP | AMRN | AMRN | 31408*OVERTON 345 to 31409 OVERTON 161 CKT 1 | 300 | 101.9952 | 102.1033 | Multiple Outage Contingency: 96120 5THMHIL 161 to 96126 5MOBTAP 161 CKT 1 96126 5MOBTAP 161 to 96499 5HINTON 161 CKT 1
10WP | MEC | MEC | 64648 HOPE MD8 69 to 63719 HOPE 5 161 CKT 1 | 105 | 102.1163 | 102.1678 | 64201 WEBSTER5 161 to 64220 WRIGHT 5 161 CKT 1
10WP | OPPD | OPPD | 65390 S1263T1T 161 to 65627 W BROCK8 69 CKT 1 | 53 | 115.1394 | 115.2353 | 64863 HUMBOLT5 161 to 65391 S975T4 T 161 CKT 1
10WP | OPPD | OPPD | 65390 S1263T1T 161 to 65627 W BROCK8 69 CKT 1 | 53 | 115.1327 | 115.2285 | 65391 S975T4 T 161 to 65575 S975 8 69 CKT 1
10WP | OPPD | OPPD | 65463 S1263 5 161 to 65390 S1263T1T 161 CKT 1 | 53 | 118.7335 | 118.8323 | 64863 HUMBOLT5 161 to 65391 S975T4 T 161 CKT 1
10WP | OPPD | OPPD | 65463 S1263 5 161 to 65390 S1263T1T 161 CKT 1 | 53 | 118.7298 | 118.8286 | 65391 S975T4 T 161 to 65575 S975 8 69 CKT 1
10WP | AECI | AECI | 96108 5OSCEOL 161 WND 2 OSCEOLA 1 | 56 | 102.1541 | 102.2832 | Multiple Outage Contingency: 96555 5GRAVOI 161 to 96552 5EDMONS 161 CKT 1 96555 5GRAVOI 161 to 96057 5BARNET 161 CKT 1
10WP | AECI | AECI | 96120 5THMHIL 161 to 961265MOBTAP 161 CKT 1 | 386 | 100.3835 | 100.4974 | Multiple Outage Contingency: 96049 7THOMHL 345 to 96044 7MCCRED 345 CKT 1 96044 7MCCRED 345 to 96043 7KINGDM 345 CKT 1
10WP | AECI | AECI | 96692 2CLINTN 69 to 96701 2GAINES 69 CKT 1 | 43 | 112.3226 | 112.5363 | Multiple Outage Contingency: 96071 5CLINTN 161 to 96108 5OSCEOL 161 CKT 1 96108 5OSCEOL 161 to 52698 STOCKTN5161 CKT 1
10WP | AECI | AECI | 96692 2CLINTN 69 to 96701 2GAINES 69 CKT 1 | 43 | 104.2146 | 104.4507 | 96071 5CLINTN 161 to 96108 5OSCEOL 161 CKT 1

## Table 3
Study Case | From Area | To Area | Monitored Branch Over 100% Rate B | Monitored Branch Over 100% Rate B | Rate <MVA> | BC % Loading | TC % Loading | Outaged Branch Causing Overload | Outaged Branch Causing Overload | ATC (MW) | Solution | Cost
04G | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 128.0588 | 134.3078 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 61.3256 | 105.8808 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 849 | Solution Undetermined
04G | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 287 | 51.8102 | 101.7767 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1096 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 23.8949 | 104.9512 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1119 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 23.8473 | 104.7465 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1122 | Solution Undetermined
04G | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 68.8342 | 100.2297 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1165 | Solution Undetermined
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 89.3825 | 108.4922 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 448 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 89.3825 | 108.4922 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 448 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 86.9677 | 104.6083 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 561 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 86.9677 | 104.6083 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 561 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 61.177 | 120.4458 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 641 | Solution Undetermined
04SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 75.8646 | 118.1058 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 693 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.1793 | 115.3291 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 725 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 79.5277 | 108.1188 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 734 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 78.0831 | 105.1867 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 820 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 72.0583 | 107.6152 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 833 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 31.2196 | 112.45 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 854 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 71.2839 | 106.813 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 857 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 53.5333 | 108.8119 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 871 | Solution Undetermined
04SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 72.303 | 105.3333 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 897 | Solution Undetermined
04SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 61.5085 | 105.5967 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 903 | Solution Undetermined
04SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 60.1446 | 104.1889 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 926 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 47.0986 | 106.0603 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 932 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 50.3407 | 107.9591 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 934 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 18.8479 | 111.1576 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 944 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 49.0751 | 105.2298 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1001 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 49.4909 | 104.7177 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 1018 | Solution Undetermined
04SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 74.9286 | 102.3414 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1046 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.375 | 101.4217 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1062 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 20.9385 | 108.8463 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1076 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 20.8952 | 108.6301 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1079 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 19.9992 | 102.5785 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1116 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 48.2291 | 101.9917 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1121 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 8.12 | 100.9991 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1174 | Solution Undetermined
04SP | OKGE | OKGE | ADA OC PUMP TAP - LULA 69KV | 55190 AOCPT 2 69 to 55191 LULA 2 69 CKT 1 | 48 | 116.5913 | 116.6505 | VALLY VIEW - VALLY VIEW TAP 69KV CKT 1 | 55181 VALYVUT2 69 to 55182 VALLYVU2 69 CKT 1 | 1200 | Invalid Contingency
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 24.4963 | 111.3022 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1042 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 24.4456 | 111.074 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1045 | Solution Undetermined
04SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 70.4239 | 101.5032 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1123 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 40.7022 | 101.5963 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1164 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 51.6201 | 100.5065 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1185 | Solution Undetermined
04FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 131.8651 | 138.6012 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID269.0 to 54725 HEMLKTP269.0 CKT 1 | 48 | 101.6661 | 102.4583 | SOUTH 4TH ST 138/69KV TRANSFORMER CKT 1 | 54730 SO4TH2 269.0 to 54731 SO4TH4 4 138 to 55758 SO4TH 1113.2 CKT 1 | 0 | Possible Invalid Contingency
04FA | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 98.4895 | 101.0501 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 755 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 15.8973 | 102.4017 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1167 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 15.8644 | 102.179 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1170 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 61.3903 | 106.9222 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1045 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 17.4973 | 104.2902 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1141 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 17.4595 | 104.0793 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1144 | Solution Undetermined
05G | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 121.5266 | 129.9813 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 25.6171 | 111.5113 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1017 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 25.5644 | 111.2824 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1021 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 38.382 | 104.0455 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1071 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 14.4364 | 102.1997 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1152 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 23.8727 | 100.2539 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1193 | Solution Undetermined
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 95.1656 | 116.882 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 202 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 95.1656 | 116.882 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 202 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 92.5793 | 112.3642 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 313 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 92.5793 | 112.3642 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 313 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 82.828 | 129.8523 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 553 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 81.2205 | 112.1448 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 667 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 58.8161 | 117.5259 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 699 | Solution Undetermined
05SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 60.7934 | 100.584 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 750 | May be able to increase CTR (if relays will coordinate) at Shawnee sub. | 5000
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 79.604 | 108.7057 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 753 | Solution Undetermined
05SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 92.877 | 99.7896 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT1 | 772.6075 | At 800 MW the loading 100.3% and the facility is relieved by additional 200 MW, Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 78.1559 | 114.8452 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 786 | Solution Undetermined
05SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 1 PAOLI 1 1 | 50 | 92.7254 | 99.6396 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT1 | 786.0458 | At 800 MW the loading 100.2% and the facility is relieved by additional 200 MW, Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 53.5109 | 112.0373 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 788 | Solution Undetermined
05SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 69.6758 | 98.8043 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 808.195 | At 1000 MW the loading 102.4% and the facility is relieved by additional 200 MW, Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 76.6436 | 110.0406 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 813 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 66.6153 | 113.0913 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 846 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 30.3718 | 112.9355 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 849 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 64.2971 | 113.6967 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 853 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 51.2378 | 110.0297 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 889 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 72.2812 | 105.2649 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 895 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 52.6718 | 110.5808 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 915 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 70.3097 | 103.0015 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 935 | Solution Undetermined
05SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 68.627 | 104.7184 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 936 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 17.4765 | 111.0196 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 942 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 58.464 | 105.0975 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 943 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 49.9485 | 107.2728 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 948 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 74.3875 | 102.853 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 949 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 69.1638 | 101.7593 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 957 | Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 64.6159 | 102.6783 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 962 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 50.3789 | 106.4434 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 963 | Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 66.2283 | 102.1575 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 963 | Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 56.1242 | 100.5014 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 999 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 49.0933 | 103.6777 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1047 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 43.8857 | 102.1278 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 1068 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 18.2707 | 106.5145 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1109 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 18.2325 | 106.2998 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1112 | Solution Undetermined
05SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 18.5641 | 102.3042 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1118 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.1128 | 100.0275 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1197 | Solution Undetermined
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 95.6503 | 124.478 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 49.7272 | 118.3921 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SH | OKGE | OKGE | PECAN CREEK 345/161KV TRANSFORMER | 55235 PECANCK7 345 WND 2 PECANCK1 1 | 370 | 100.4441 | 102.288 | FT SMITH - MUSKOGEE 345KV CKT 1 | 55224 MUSKOGE7 345 to 55302 FTSMITH7 345 CKT 1 | 0 | Add 2nd 345/161 kV 369MVA transformer. | 3000000
05SH | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 94.677 | 116.1 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 105 | Solution Undetermined
05SH | OKGE | OKGE | PECAN CREEK 345/161KV TRANSFORMER | 55234 PECANCK5 161 WND 1 PECANCK1 1 | 370 | 99.2108 | 100.996 | FT SMITH - MUSKOGEE 345KV CKT 1 | 55224 MUSKOGE7 345 to 55302 FTSMITH7 345 CKT 1 | 296 | See Previous Upgrade Specified
05SH | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 84.612 | 101.3424 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 720 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 76.7064 | 108.4902 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 769 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 72.3026 | 104.0134 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 1005 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 56.3409 | 105.6108 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1045 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 23.1872 | 109.9764 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1060 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 23.1392 | 109.7554 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1063 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 44.4938 | 105.5133 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1081 | Solution Undetermined
05FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 122.2519 | 128.7736 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05FA | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 93.7042 | 104.6854 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 266 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 13.5194 | 100.4148 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1194 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 13.4907 | 100.2042 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1197 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 22.6271 | 109.0302 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1075 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 22.5793 | 108.8081 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1078 | Solution Undetermined
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 96.9575 | 123.0482 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 133 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 96.9575 | 123.0482 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 133 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 94.1343 | 117.8324 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 261 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 94.1343 | 117.8324 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 261 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 95.5738 | 104.2151 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 460 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 95.4116 | 104.0547 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 483 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 81.5991 | 135.5241 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 571 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 83.1507 | 117.2839 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 600 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 94.0801 | 102.6304 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 637 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 93.9284 | 102.485 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 650 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 59.8058 | 124.3562 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 671 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 81.4682 | 113.3307 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 684 | Solution Undetermined
07SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 62.2874 | 111.4199 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 700 | See Previous Upgrade Specified
07SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55074 FRSTHIL2 69 to 55071 TECUMSH2 69 CKT 1 | 72 | 71.8761 | 107.7186 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 729 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 54.2323 | 118.539 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 762 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 77.9456 | 117.2993 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 807 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 78.2366 | 120.3276 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 817 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 29.275 | 117.6526 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 828 | Solution Undetermined
07SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 98.3301 | 102.0828 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 852 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 52.0315 | 114.5199 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 853 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 66.3383 | 120.5308 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 872 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 86.6782 | 104.325 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 879 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 63.7734 | 120.9346 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 882 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 76.1786 | 107.6193 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 889 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 73.2926 | 112.1553 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 893 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 50.7247 | 111.6398 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 906 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 51.1654 | 110.3893 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 914 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.4414 | 106.2683 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 917 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 15.6526 | 114.5077 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 924 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 71.1877 | 109.6554 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 933 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 51.2321 | 117.5561 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 957 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 44.1187 | 108.0189 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 964 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 58.3025 | 112.5134 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 970 | Solution Undetermined
07SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 68.1178 | 109.5127 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 971 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 49.8622 | 107.4988 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 975 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 67.0005 | 108.913 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 979 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 65.2222 | 109.293 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 983 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 74.6599 | 103.8427 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 983 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 69.9653 | 108.3095 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1021 | Solution Undetermined
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 16.1156 | 105.7521 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1052 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 56.1024 | 106.9398 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1065 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 48.0189 | 104.0258 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1070 | Solution Undetermined
07SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 75.4536 | 105.5218 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1074 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 60.7476 | 104.5231 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1090 | Solution Undetermined
07SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 67.2444 | 102.5657 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 1094 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 68.171 | 102.5846 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1104 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 61.2085 | 103.1529 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1121 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - HAYMAKER 138KV | 54898 CIMARON4 138 to 54863 HAYMAKR4 138 CKT 1 | 308 | 73.1158 | 101.4585 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 1125 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 66.5057 | 101.7953 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 1126 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 16.6609 | 105.3371 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1128 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 16.6256 | 105.1213 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1131 | Solution Undetermined
07SP | OKGE | OKGE | HEFNER - TULSA 138KV | 54847 TULSA 4 138 to 54848 HEFNER 4 138 CKT 1 | 222 | 80.7824 | 101.1194 | 84TH ST - TENNESSEE TAP 138KV | 54837 TENESTP4 138 to 54843 84TH ST4 138 CKT 1 | 1144 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 3.1828 | 102.4003 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1149 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 17.8668 | 100.4984 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 1184 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 16.539 | 100.2495 | DRAPER LAKE - POOST ROAD 138KV | 54933 DRAPER 4 138 to 54965 POSTRDT4 138 CKT 1 | 1192 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 17.7807 | 100.2318 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1193 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 19.87 | 107.2834 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1099 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 19.8284 | 107.0652 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1101 | Solution Undetermined
10SP | OKGE | AEPW | BONANZA - BONANZA TAP 161KV | 55261 BONANZT5 161 to 53126 BONANZA5 161 CKT 1 | 177 | 101.898 | 102.2532 | AES - TARBY 161KV | 55262 AES 5 161 to 55264 TARBY 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 100.8972 | 129.5462 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 0 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 100.8972 | 129.5462 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 0 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 101.2712 | 104.9279 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 97.791 | 123.9418 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 96 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 97.791 | 123.9418 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 96 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 97.9722 | 106.8968 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 212 | Solution Undetermined
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 97.7933 | 106.7185 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 230 | Solution Undetermined
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 96.3101 | 105.0008 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 373 | Solution Undetermined
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 96.1428 | 104.8355 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 390 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 85.7349 | 120.3134 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 523 | Solution Undetermined
10SP | OKGE | OKGE | PECAN CREEK 345/161KV TRANSFORMER | 55235 PECANCK7 345 WND 2 PECANCK1 1 | 370 | 98.3568 | 101.2326 | CLARKSVILLE - MUSKOGEE 345KV | 53756 CLARKSV7 345 to 55224 MUSKOGE7 345 CKT 1 | 576 | See Previous Upgrade Specified
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 83.9234 | 116.1437 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 607 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 78.0633 | 133.62 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 684 | Solution Undetermined
10SP | OKGE | OKGE | POOST ROAD - SE15TH 138KV | 54993 SE15TH 4 138 to 54965 POSTRDT4 138 CKT 1 | 191 | 58.1334 | 115.4451 | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 704 | May Limit Renewal Rights
10SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 72.4167 | 109.5069 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 730 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.6145 | 121.3671 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 737 | Solution Undetermined
10SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 59.5553 | 110.3927 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 771 | See Previous Upgrade Specified
10SP | OKGE | OKGE | MAUD - SEMINOLE 138KV CKT 2 | 55055 MAUD 4 138 to 55044 SEMINOL4 138 CKT 2 | 287 | 80.5556 | 104.0941 | MAUD - SEMINOLE 138KV CKT 1 | 55044 SEMINOL4 138 to 55055 MAUD 4 138 CKT 1 | 791 | May Limit Renewal Rights
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 78.5371 | 110.3899 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 825 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 76.8596 | 116.8579 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 832 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 76.6962 | 120.0514 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 837 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 59.7839 | 107.9148 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 839 | May Limit Renewal Rights
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 53.0039 | 116.236 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 841 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 28.0806 | 117.5773 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 863 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 49.9546 | 114.412 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 863 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 51.6692 | 113.317 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 892 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 52.0955 | 111.9302 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 900 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 76.8968 | 106.3977 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 923 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 81.8173 | 104.4898 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 924 | May Limit Renewal Rights
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 62.888 | 118.6279 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 925 | Solution Undetermined
10SP | OKGE | OKGE | PECAN CREEK 345/161KV TRANSFORMER | 55235 PECANCK7 345 WND 2 PECANCK1 1 | 370 | 96.8616 | 100.581 | FT SMITH - MUSKOGEE 345KV CKT 1 | 55224 MUSKOGE7 345 to 55302 FTSMITH7 345 CKT 1 | 937 | See Previous Upgrade Specified
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 71.9638 | 111.4564 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 938 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 59.8927 | 118.6218 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 941 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 86.1912 | 103.4081 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 951 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 50.7642 | 108.9976 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 958 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 12.5502 | 112.6273 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 969 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 69.739 | 108.8562 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 989 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 55.284 | 104.0863 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1000 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 63.4423 | 108.6852 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1038 | Solution Undetermined
10SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 65.9224 | 108.5708 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1038 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 46.1293 | 114.4571 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1038 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 65.528 | 108.6073 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1046 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 54.1657 | 109.8027 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1059 | Solution Undetermined
10SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 12.9396 | 103.8247 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1111 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 53.4729 | 105.7632 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1119 | Solution Undetermined
10SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 66.6765 | 102.3259 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 1122 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 308 | 73.0991 | 101.9628 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 1135 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 68.4529 | 107.443 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1144 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 67.0027 | 102.0297 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1144 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 58.1783 | 102.8277 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1147 | Solution Undetermined
10SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 65.8945 | 101.5098 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 1149 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 37.8424 | 101.8379 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 1149 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 59.2572 | 102.2644 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1159 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 44.704 | 101.0578 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1171 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 12.4723 | 101.1943 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1184 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 12.4442 | 100.983 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1187 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 16.3051 | 100.1248 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 1196 | Solution Undetermined
10SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 82.1442 | 100.0052 | INGLEWOOD - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55060 INGLEWD4 138 CKT 1 | 1199 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 84.9662 | 170.6205 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 124.5944 | 164.0878 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 67.2348 | 101.2862 | DRAPER LAKE - GM 138KV | 54933 DRAPER 4 138 to 54961 GM 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 69.0425 | 100.5515 | DRAPER LAKE - MIDWEST TAP 138KV | 54933 DRAPER 4 138 to 54946 MIDWEST4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10WP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 72.0542 | 104.7666 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 585 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 19.6757 | 104.8686 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1132 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 19.635 | 104.6486 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1135 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 31.1209 | 102.6538 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1138 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 41.3943 | 101.1704 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1165 | Solution Undetermined
[11 empty] | Total Cost | 3005000

## Table 4
Study Case | From Area | To Area | Monitored Branch Over 100% Rate B | Monitored Branch Over 100% Rate B | Rate <MVA> | BC % Loading | TC % Loading | Outaged Branch Causing Overload | Outaged Branch Causing Overload | ATC (MW) | Solution | Cost
04G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 61.5437 | 106.1055 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 880 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 32.4515 | 113.796 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 968 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 32.3866 | 113.583 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 971 | Solution Undetermined
04G | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 287 | 50.3913 | 100.9386 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1148 | Solution Undetermined
04SP | OKGE | OKGE | FT SMITH 500/161KV TRANSFORMER | 55305 FTSMITH8 500 WND 2 FTSMITH3 1 | 480 | 101.8088 | 102.4499 | FT SMITH 345/161KV TRANSFORMER CKT 1 | 55300 FTSMITH5 161 to 55302 FTSMITH7 345 to 55728 FTSMIT3113.8 CKT 1 | 0 | OKGE Plans to Install 2nd 500-161kV transformer bank by 12/1/2004
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 88.2839 | 107.7661 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 489 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 88.2839 | 107.7661 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 489 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 85.9134 | 103.809 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 602 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 85.9134 | 103.809 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 602 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 59.6685 | 119.6317 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 658 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 54.669 | 114.478 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 742 | Solution Undetermined
04SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 69.8261 | 112.3307 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 806 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 30.0885 | 112.2662 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 862 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 21.0227 | 114.0066 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 890 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 69.0944 | 105.2105 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 907 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 74.6903 | 103.5414 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 909 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 51.221 | 107.1008 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 913 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 68.3151 | 104.4045 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 930 | Solution Undetermined
04SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 78.2681 | 106.1068 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 942 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 45.5986 | 105.1447 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 959 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 28.7 | 117.0157 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 964 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 48.2782 | 106.7604 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 966 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 28.6409 | 116.7884 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 967 | Solution Undetermined
04SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 67.7829 | 101.1464 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 983 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 22.7806 | 105.8256 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1011 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 14.3713 | 107.3344 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1018 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 47.0652 | 104.0273 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1047 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 47.5073 | 103.2449 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 1075 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 73.4814 | 100.8066 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 1078 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 287 | 48.6877 | 101.8094 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1148 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 51.5304 | 100.6302 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1165 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 46.2981 | 100.5389 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1179 | Solution Undetermined
04SP | OKGE | OKGE | ADA OC PUMP TAP - LULA 69KV | 55190 AOCPT 2 69 to 55191 LULA 2 69 CKT 1 | 48 | 116.3908 | 116.5262 | VALLY VIEW - VALLY VIEW TAP 69KV CKT 1 | 55181 VALYVUT2 69 to 55182 VALLYVU2 69 CKT 1 | 1200 | Invalid Contingency
04SH | OKGE | OKGE | CLEVELAND TAP - SOUTH 4TH ST 69KV | 54730 SO4TH2 2 69 to 54722 CLEVETP2 69 CKT 1 | 92 | 102.8481 | 106.2687 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 32.1722 | 119.1601 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 934 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 32.1057 | 118.9261 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 937 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 43.1373 | 104.3554 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1100 | Solution Undetermined
04SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 68.7767 | 100.2916 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1184 | Solution Undetermined
04SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 40.651 | 100.3743 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1191 | Solution Undetermined
04FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 164.5359 | 171.3184 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID269.0 to 54725 HEMLKTP269.0 CKT 1 | 48 | 109.2454 | 110.0101 | SOUTH 4TH ST 138/69KV TRANSFORMER CKT 1 | 54730 SO4TH2 269.0 to 54731 SO4TH4 4 138 to 55758 SO4TH 1113.2 CKT 1 | 0 | Possible Invalid Contingency
04FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID2 69 to 54725 HEMLKTP2 69 CKT 1 | 48 | 100.436 | 102.0382 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 23.4884 | 109.9903 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1062 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 23.4398 | 109.7643 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1065 | Solution Undetermined
04FA | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 69.7295 | 101.7149 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1132 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 49.8559 | 100.24 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1194 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 63.7476 | 110.0539 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 965 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 25.3252 | 112.9266 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1024 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 25.2729 | 112.7062 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1027 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 60.7908 | 103.4886 | KETCH - OMPA-FAIRVIEW 138KV | 54834 KETCH 4 138 to 56173 OMFAIRF4 138 CKT 1 | 1123 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 36.5812 | 102.8784 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1147 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 53.0289 | 101.9957 | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 1157 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 52.456 | 101.7069 | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 1164 | Solution Undetermined
05AP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 30.9226 | 107.6095 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1093 | Solution Undetermined
05AP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 30.8586 | 107.3962 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1096 | Solution Undetermined
05G | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 169.0068 | 178.1158 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 33.4063 | 120.1483 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 905 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 33.3372 | 119.9216 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 907 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 41.6091 | 107.4758 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 982 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 15.1628 | 106.0769 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1073 | Solution Undetermined
05G | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 13.6622 | 104.8472 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1092 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 44.0408 | 101.1985 | KETCH - OMPA-FAIRVIEW 138KV | 54834 KETCH 4 138 to 56173 OMFAIRF4 138 CKT 1 | 1164 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 22.089 | 100.6809 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1182 | Solution Undetermined
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 94.4754 | 116.4696 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 232 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 94.4754 | 116.4696 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 232 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 91.9321 | 111.8861 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 342 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 91.9321 | 111.8861 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 342 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 75.9484 | 123.3339 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 694 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.5048 | 116.7843 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 713 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 77.0861 | 108.2266 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 796 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 52.1982 | 111.2862 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 804 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 29.6824 | 112.905 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 852 | Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 73.039 | 110.0926 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 862 | Solution Undetermined
05SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 68.5135 | 98.1043 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 871.3856 | At 1000 MW the loading 101.7% and the facility is relieved by additional 200 MW, Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 75.7172 | 105.0142 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 879 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 20.2449 | 114.1561 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 887 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 49.4274 | 109.0143 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 913 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 69.8319 | 103.7016 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 927 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 56.7223 | 106.5995 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 930 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 58.1067 | 105.1095 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 937 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 46.5018 | 104.8497 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 964 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 48.1835 | 106.265 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 971 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 26.5458 | 115.2247 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 989 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 26.4909 | 114.998 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 991 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 48.6467 | 105.1755 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 993 | Solution Undetermined
05SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 21.6119 | 105.9117 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 995 | Solution Undetermined
05SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 12.6212 | 106.7518 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1021 | Solution Undetermined
05SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 75.8291 | 102.7548 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1022 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 47.4064 | 102.418 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1099 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 42.5832 | 101.3424 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 1117 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 40.2523 | 100.7154 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1178 | Solution Undetermined
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 93.5907 | 122.8359 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 42.0721 | 111.573 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SH | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 88.1225 | 109.8063 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 243 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 75.4671 | 107.7165 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 823 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 31.409 | 118.5771 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 942 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 31.344 | 118.3508 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 944 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 47.3634 | 109.1564 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1011 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 55.8267 | 105.6751 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1045 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 71.0608 | 103.2044 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 1047 | Solution Undetermined
05SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 44.7242 | 104.8238 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1096 | Solution Undetermined
05SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 52.8015 | 101.8163 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1149 | Solution Undetermined
05FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 166.1148 | 172.6099 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID269.0 to 54725 HEMLKTP269.0 CKT 1 | 48 | 107.9604 | 108.9074 | SOUTH 4TH ST 138/69KV TRANSFORMER CKT 1 | 54730 SO4TH2 269.0 to 54731 SO4TH4 4 138 to 55758 SO4TH 1113.2 CKT 1 | 0 | Possible Invalid Contingency
05FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID2 69 to 54725 HEMLKTP2 69 CKT 1 | 48 | 99.2006 | 100.9681 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 510 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 21.8322 | 108.8726 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1077 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 21.7871 | 108.6478 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1080 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 28.2728 | 100.1343 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1196 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 30.5454 | 117.4094 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 960 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 30.4819 | 117.1807 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 963 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 51.427 | 103.1354 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1130 | Solution Undetermined
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 95.9615 | 122.2165 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 179 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 95.9615 | 122.2165 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 179 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 93.1955 | 116.9579 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 303 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 93.1955 | 116.9579 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 303 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 93.8705 | 102.7949 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 656 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 93.7072 | 102.6321 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 671 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 58.8558 | 123.8627 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 681 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 79.202 | 113.4865 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 728 | Solution Undetermined
07SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 60.4663 | 109.8766 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 734 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 75.0257 | 129.2604 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 737 | Solution Undetermined
07SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55074 FRSTHIL2 69 to 55071 TECUMSH2 69 CKT 1 | 72 | 70.5893 | 106.7766 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 759 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 53.2635 | 118.0205 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 773 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 92.3243 | 101.007 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 796 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 98.4736 | 102.4687 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 803 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 77.7699 | 109.7738 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 810 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 92.1715 | 100.8562 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 821 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 28.8419 | 117.6625 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 834 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 18.5162 | 117.6374 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 878 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 50.1491 | 113.3584 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 879 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 40.4017 | 103.5828 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 879 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 73.3585 | 115.7691 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 881 | Solution Undetermined
07SP | OKGE | OKGE | EARLSBORO - FOREST HILL 69KV | 55073 ERLSBOR2 69 to 55074 FRSTHIL2 69 CKT 1 | 48 | 47.1237 | 104.0189 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 906 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 71.3084 | 111.1361 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 915 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 48.8903 | 110.5086 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 930 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 49.3579 | 108.9542 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 946 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 56.462 | 114.018 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 954 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 58.0682 | 112.7002 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 958 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 84.9922 | 102.9301 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 969 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 19.513 | 109.5998 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 969 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 43.1224 | 107.4509 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 974 | Solution Undetermined
07SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 79.2761 | 109.6917 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 979 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 72.5694 | 104.1291 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 993 | Solution Undetermined
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 9.71 | 109.2279 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1003 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 66.6282 | 105.8964 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 1005 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 45.3695 | 112.0363 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1006 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 25.0201 | 114.1933 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1009 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 48.1027 | 106.0925 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1009 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 24.9684 | 113.9652 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1012 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 53.8231 | 103.0551 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1033 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 52.2301 | 106.8463 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1057 | Solution Undetermined
07SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 63.2031 | 104.8934 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1069 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 64.4936 | 103.3916 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 1085 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 59.8577 | 104.267 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1093 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 60.9542 | 103.2288 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1113 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 46.0915 | 102.4261 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1120 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 63.263 | 102.0132 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1131 | Solution Undetermined
07SP | OKGE | OMPA | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 287 | 48.5668 | 101.8728 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1140 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 51.7743 | 102.9243 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1142 | Solution Undetermined
07SP | OKGE | OKGE | HEFNER - TULSA 138KV | 54847 TULSA 4 138 to 54848 HEFNER 4 138 CKT 1 | 222 | 80.2336 | 100.8829 | 84TH ST - TENNESSEE TAP 138KV | 54837 TENESTP4 138 to 54843 84TH ST4 138 CKT 1 | 1155 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 71.2908 | 100.5835 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1165 | Solution Undetermined
07SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 64.607 | 100.2499 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 1190 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 39.9895 | 100.2484 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1193 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 60.2251 | 104.1571 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1196 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 27.8666 | 115.6276 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 963 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 27.9245 | 115.8535 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 980 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 14.8704 | 103.109 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1126 | Solution Undetermined
10SP | OKGE | OKGE | 3RDST - MULDROW 69KV | 55256 MULDROW2 69 to 55307 3RDST 2 69 CKT 1 | 48 | 102.2882 | 102.7128 | KILGORE - VBI 69KV | 55335 KILGORE2 69 to 55336 VBI 2 69 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | SWPA | BROWN - BROWN 138KV | 55157 BROWN 4 138 to 52802 S BROWN4 138 CKT 1 | 120 | 100.0467 | 101.6967 | GLASSES - RUSSETT 138KV | 55120 RUSSET-4 138 to 55147 GLASSES4 138 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | COLONY - FT SMITH 161KV | 55345 COLONY 5 161 to 55300 FTSMITH5 161 CKT 1 | 335 | 102.1739 | 102.509 | FT SMITH - QUANEX TAP 161KV | 55300 FTSMITH5 161 to 55310 QUANXTP5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | MASSARD 161/69KV TRANSFORMER | 55343 MASSARD5 161 WND 2 MASSARD4 1 | 120 | 103.7371 | 104.0074 | ARKOMA - FTSMITH 161KV CKT 1 | 55300 FTSMITH5 161 to 55306 ARKOMA 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | MASSARD 161/69KV TRANSFORMER | 55342 MASSARD269.0 WND 1 MASSARD4 1 | 120 | 101.1674 | 101.4297 | ARKOMA - FTSMITH 161KV CKT 1 | 55300 FTSMITH5 161 to 55306 ARKOMA 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | MASSARD 161/69KV TRANSFORMER | 55343 MASSARD5 161 WND 2 MASSARD4 1 | 120 | 100.1216 | 100.393 | 3RDST - ARKOMA 161KV CKT 1 | 55306 ARKOMA 5 161 to 55308 3RDST 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 101.3079 | 105.0732 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 99.5302 | 128.3498 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 20 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 99.5302 | 128.3498 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 20 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 96.4917 | 122.7959 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 153 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 96.4917 | 122.7959 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 153 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 96.1583 | 105.2395 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 403 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 95.978 | 105.0597 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 422 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 94.435 | 103.2508 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 582 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 94.2665 | 103.0841 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 601 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 82.0175 | 116.8016 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 646 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 80.2657 | 112.7103 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 735 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 55.5703 | 120.5268 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 754 | Solution Undetermined
10SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 70.6619 | 108.1163 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 777 | Solution Undetermined
10SP | OKGE | OKGE | POOST ROAD - SE15TH 138KV | 54993 SE15TH 4 138 to 54965 POSTRDT4 138 CKT 1 | 191 | 52.4634 | 110.556 | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 813 | May Limit Renewal Rights
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 70.8513 | 126.7631 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 823 | Solution Undetermined
10SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 57.0592 | 108.2949 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 826 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 51.3943 | 114.8822 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 868 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 27.3033 | 117.1419 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 872 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 48.8998 | 113.5673 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 880 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 50.1022 | 111.9917 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 919 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 15.3186 | 115.658 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 926 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 71.3859 | 114.9964 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 929 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 50.51 | 110.4737 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 932 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 75.1185 | 107.1682 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 932 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 55.2346 | 103.9961 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 940 | May Limit Renewal Rights
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 287 | 39.8262 | 108.5196 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 964 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 80.4104 | 103.319 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 970 | May Limit Renewal Rights
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 69.8248 | 110.2263 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 973 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 49.2213 | 107.5708 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 989 | Solution Undetermined
10SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 16.185 | 107.3294 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1029 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 52.0671 | 111.2095 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1043 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 54.0566 | 110.2543 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1047 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 73.5358 | 103.2539 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1049 | Solution Undetermined
10SP | OKGE | OKGE | EARLSBORO - FOREST HILL 69KV | 55073 ERLSBOR2 69 to 55074 FRSTHIL2 69 CKT 1 | 48 | 43.0434 | 101.7676 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 1055 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 21.4115 | 110.3862 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1061 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 21.3674 | 110.164 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1064 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 84.4569 | 101.7717 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1069 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 64.9069 | 104.7712 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 1090 | Solution Undetermined
10SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 4.6249 | 105.5031 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1091 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 39.8735 | 103.4775 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1124 | Solution Undetermined
10SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 60.5662 | 103.4857 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1135 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 57.7623 | 103.2456 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1143 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 47.6424 | 103.699 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1147 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 62.6482 | 102.1537 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 1150 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 59.1073 | 102.4619 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1154 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 57.4893 | 102.2388 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1158 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 51.6736 | 100.6286 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1170 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 36.7955 | 100.9766 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 1173 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 48.9303 | 101.4039 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1180 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 61.3544 | 100.7314 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1183 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 39.4549 | 100.2474 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1194 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 43.9596 | 100.1333 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1198 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 75.7863 | 162.5734 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 121.735 | 161.6166 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 27.8062 | 113.0445 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1019 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 27.7488 | 112.8165 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1022 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 33.4815 | 105.6173 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1070 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 40.452 | 100.9484 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1172 | Solution Undetermined
[11 empty] | Total Cost | 0

## Table 5
Study Case | From Area | To Area | Monitored Branch Over 100% Rate B | Monitored Branch Over 100% Rate B | Rate <MVA> | BC % Loading | TC % Loading | Outaged Branch Causing Overload | Outaged Branch Causing Overload | ATC (MW) | Solution | Cost
04G | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 155.299 | 162.4094 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04G | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 287 | 64.0015 | 114.7295 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 742 | Solution Undetermined
04G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 66.5345 | 111.4137 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 748 | Solution Undetermined
04G | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 71.5605 | 103.3419 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 914 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 35.7162 | 116.906 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 917 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 35.6448 | 116.6827 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 920 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - HORSESHOE LAKE 138KV | 54907 ARCADIA4 138 to 54941 HSL 4 138 CKT 1 | 287 | 42.3592 | 102.2025 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1139 | Solution Undetermined
04G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 57.929 | 100.9152 | KETCH - OMPA-FAIRVIEW 138KV | 54834 KETCH 4 138 to 56173 OMFAIRF4 138 CKT 1 | 1146 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - HORSESHOE LAKE 138KV | 54907 ARCADIA4 138 to 54941 HSL 4 138 CKT 1 | 287 | 52.9586 | 100.5813 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1175 | Solution Undetermined
04G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 52.9549 | 100.414 | ARCADIA - HORSESHOE LAKE 138KV | 54907 ARCADIA4 138 to 54941 HSL 4 138 CKT 1 | 1180 | Solution Undetermined
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 87.6328 | 107.0291 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 513 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 87.6328 | 107.0291 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 513 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 64.4607 | 124.116 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 582 | Solution Undetermined
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 85.278 | 103.1572 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 628 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 85.278 | 103.1572 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 628 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 59.4684 | 118.9846 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 666 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 80.1048 | 108.8351 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 711 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 74.3187 | 110.2437 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 763 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.4122 | 113.0396 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 779 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 73.5407 | 109.439 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 784 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 34.1891 | 116.0008 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 785 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 78.7003 | 105.8647 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 791 | Solution Undetermined
04SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 70.051 | 112.5661 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 802 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 50.4084 | 109.7027 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 832 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 23.7069 | 116.4774 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 842 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 287 | 61.9354 | 114.9635 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 879 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 51.5762 | 109.7243 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 889 | Solution Undetermined
04SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 81.153 | 108.7723 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 889 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 32.0798 | 120.1404 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 922 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 32.0134 | 119.9123 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 925 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 25.8726 | 108.7624 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 938 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 58.1457 | 107.0491 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 939 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 50.2798 | 106.9555 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 956 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 50.7402 | 106.2258 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 971 | Solution Undetermined
04SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 67.98 | 101.2835 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 980 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 16.079 | 108.9619 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 981 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.6372 | 101.9911 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1009 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 65.3397 | 102.46 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1053 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 58.5773 | 102.2005 | QUAIL CREEK - SKYLINE 138KV | 54850 SKYLINE4 138 to 54851 QUAILCK4 138 CKT 1 | 1058 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 49.4474 | 103.4476 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1064 | Solution Undetermined
04SP | OKGE | OMPA | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 287 | 52.4492 | 101.5375 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1114 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 73.7442 | 100.3054 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1151 | Solution Undetermined
04SP | OKGE | OKGE | ADA OC PUMP TAP - LULA 69KV | 55190 AOCPT 2 69 to 55191 LULA 2 69 CKT 1 | 48 | 116.6409 | 116.7344 | VALLY VIEW - VALLY VIEW TAP 69KV CKT 1 | 55181 VALYVUT2 69 to 55182 VALLYVU2 69 CKT 1 | 1200 | Invalid Contingency
04SH | OKGE | OKGE | CLEVELAND TAP - SOUTH 4TH ST 69KV | 54730 SO4TH2 2 69 to 54722 CLEVETP2 69 CKT 1 | 92 | 104.2127 | 107.6798 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 35.516 | 122.3168 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 890 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 35.4424 | 122.0709 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 893 | Solution Undetermined
04SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 73.3612 | 104.7472 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 947 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 45.6705 | 106.9311 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1041 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 54.7205 | 103.9754 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1081 | Solution Undetermined
04SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 42.2893 | 102.1074 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1150 | Solution Undetermined
04SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 69.227 | 100.569 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 1169 | Solution Undetermined
04FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 166.2433 | 173.1911 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID269.0 to 54725 HEMLKTP269.0 CKT 1 | 48 | 108.8949 | 109.7339 | SOUTH 4TH ST 138/69KV TRANSFORMER CKT 1 | 54730 SO4TH2 269.0 to 54731 SO4TH4 4 138 to 55758 SO4TH 1113.2 CKT 1 | 0 | Possible Invalid Contingency
04FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID2 69 to 54725 HEMLKTP2 69 CKT 1 | 48 | 100.2395 | 101.9056 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04FA | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 73.7162 | 105.6324 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 977 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 26.9565 | 113.4462 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1013 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 26.9005 | 113.2045 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1016 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 52.2567 | 102.7734 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1128 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 67.8344 | 113.556 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 837 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 29.4366 | 116.5469 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 974 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 29.3757 | 116.3171 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 977 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 63.3572 | 105.4914 | KETCH - OMPA-FAIRVIEW 138KV | 54834 KETCH 4 138 to 56173 OMFAIRF4 138 CKT 1 | 1076 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 56.3979 | 104.7154 | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 1097 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 39.4415 | 105.2913 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1102 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 55.6009 | 104.2147 | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 1108 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 59.733 | 101.8291 | OMPA-FAIRVIEW - SKYLINE 138KV | 54850 SKYLINE4 138 to 56173 OMFAIRF4 138 CKT 1 | 1159 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 47.8072 | 101.6569 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1161 | Solution Undetermined
04WP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 36.1527 | 100.75 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1186 | Solution Undetermined
05AP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 35.0746 | 111.5065 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1039 | Solution Undetermined
05AP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 35.0017 | 111.2768 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1042 | Solution Undetermined
05G | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 170.142 | 179.2779 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 37.4342 | 123.8882 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 853 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 37.357 | 123.644 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 856 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 45.1494 | 111.2079 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 887 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 18.4085 | 108.4143 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1027 | Solution Undetermined
05G | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 15.9879 | 106.379 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1059 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 26.5613 | 104.1817 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1088 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 46.3761 | 103.4932 | KETCH - OMPA-FAIRVIEW 138KV | 54834 KETCH 4 138 to 56173 OMFAIRF4 138 CKT 1 | 1099 | Solution Undetermined
05G | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 23.8749 | 102.6607 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1124 | Solution Undetermined
05G | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 48.5455 | 101.6308 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1129 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 33.1681 | 101.7292 | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 1153 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 33.6928 | 101.3259 | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 1164 | Solution Undetermined
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 93.8122 | 115.7609 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 258 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 93.8122 | 115.7609 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 258 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 91.2829 | 111.2683 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 368 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 91.2829 | 111.2683 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 368 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 82.7102 | 113.7085 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 615 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 61.8131 | 120.7868 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 645 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 76.258 | 123.593 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 688 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 81.1232 | 110.2282 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 697 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.5137 | 115.3052 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 734 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 33.7257 | 116.6177 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 784 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 23.0205 | 116.716 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 841 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 52.9152 | 112.157 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 842 | Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 73.296 | 110.2449 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 860 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 51.5838 | 109.3272 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 900 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 75.7607 | 104.2947 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 902 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 52.0636 | 108.3152 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 916 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 56.5205 | 106.3376 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 932 | Solution Undetermined
05SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 24.6964 | 108.7893 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 933 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 69.1469 | 102.9101 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 941 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 30.1773 | 118.5528 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 945 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 46.9087 | 105.3921 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 946 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 30.1147 | 118.321 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 947 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 56.9649 | 103.9444 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 950 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 47.3905 | 105.6361 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 958 | Solution Undetermined
05SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 78.4737 | 105.1806 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 966 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 50.7357 | 105.478 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 983 | Solution Undetermined
05SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 14.4322 | 108.4693 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 983 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 63.0271 | 102.4342 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 993 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 74.3349 | 100.9919 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1042 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 50.1559 | 101.208 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1106 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 41.5 | 101.7792 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1145 | Solution Undetermined
05SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 63.7311 | 100.0799 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1149 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.0535 | 100.1935 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1178 | Solution Undetermined
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 90.402 | 119.5817 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 37.9744 | 107.2978 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SH | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 88.1821 | 109.8885 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 239 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 79.6542 | 111.7196 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 589 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 75.2602 | 107.2348 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 844 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 35.1239 | 121.9818 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 894 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 35.0511 | 121.7428 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 896 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 59.8305 | 109.2952 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 942 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 50.0911 | 111.5627 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 954 | Solution Undetermined
05SH | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 84.2886 | 101.4881 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 1042 | Solution Undetermined
05SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 46.5287 | 106.4101 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1060 | Solution Undetermined
05SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 55.8257 | 104.6027 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1069 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 60.8512 | 101.8345 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 1139 | Solution Undetermined
05FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 169.0882 | 175.8672 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID269.0 to 54725 HEMLKTP269.0 CKT 1 | 48 | 107.6685 | 108.6947 | SOUTH 4TH ST 138/69KV TRANSFORMER CKT 1 | 54730 SO4TH2 269.0 to 54731 SO4TH4 4 138 to 55758 SO4TH 1113.2 CKT 1 | 0 | Possible Invalid Contingency
05FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID2 69 to 54725 HEMLKTP2 69 CKT 1 | 48 | 99.0341 | 100.897 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 574 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 25.4421 | 112.4086 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1028 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 25.3894 | 112.1879 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1031 | Solution Undetermined
05FA | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 55.4443 | 104.012 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1040 | Solution Undetermined
05FA | OKGE | OKGE | CLEVELAND TAP - SOUTH 4TH ST 69KV | 54730 SO4TH2 2 69 to 54722 CLEVETP2 69 CKT 1 | 92 | 97.6223 | 100.3356 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 1048 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 31.2719 | 103.2837 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1117 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 39.9855 | 100.2953 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1190 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 34.547 | 121.1283 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 908 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 34.4756 | 120.8869 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 911 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 54.2737 | 105.4423 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1075 | Solution Undetermined
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 96.7795 | 123.0345 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 142 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 96.7795 | 123.0345 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 142 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 93.9904 | 117.8231 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 268 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 93.9904 | 117.8231 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 268 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 84.4824 | 118.6798 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 554 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 62.4124 | 127.2084 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 627 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 82.8326 | 114.693 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 631 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 93.7605 | 102.581 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 681 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 93.5968 | 102.4182 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 697 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.8305 | 121.3809 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 721 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 74.8521 | 129.1463 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 732 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 32.5603 | 121.1479 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 787 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 53.8582 | 116.7618 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 812 | Solution Undetermined
07SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 55.9289 | 105.6682 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 833 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 98.3817 | 102.2302 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 835 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 21.147 | 120.1337 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 845 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 77.4094 | 108.9027 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 848 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 92.1852 | 100.7987 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 852 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 52.5057 | 113.8259 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 864 | Solution Undetermined
07SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 67.4629 | 103.7664 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 868 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 52.993 | 112.3595 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 872 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 92.0323 | 100.648 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 877 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 73.2539 | 115.6424 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 881 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 46.7084 | 110.8428 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 909 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 86.0976 | 103.8786 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 913 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.1029 | 106.1601 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 928 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 51.644 | 109.4133 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 931 | Solution Undetermined
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 21.9066 | 111.9447 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 931 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 70.3745 | 110.1382 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 933 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 75.9213 | 105.0934 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 939 | Solution Undetermined
07SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 81.2991 | 111.4569 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 946 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 55.8558 | 113.4598 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 962 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 27.8508 | 116.6974 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 976 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 56.5767 | 111.3079 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 976 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 27.7931 | 116.4625 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 978 | Solution Undetermined
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 10.9756 | 110.5581 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 982 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 50.3436 | 106.542 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 993 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 45.7613 | 112.421 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1006 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 63.4839 | 107.303 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1021 | Solution Undetermined
07SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 68.3659 | 103.8816 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 1041 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 65.697 | 104.9542 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 1042 | Solution Undetermined
07SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 67.6251 | 103.1008 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 1072 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 51.6369 | 106.2877 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1074 | Solution Undetermined
07SP | OKGE | OMPA | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 287 | 50.7761 | 103.9175 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1075 | Solution Undetermined
07SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 63.0951 | 104.789 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1076 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 41.9532 | 104.9512 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1081 | Solution Undetermined
07SP | OKGE | OKGE | HEFNER - TULSA 138KV | 54847 TULSA 4 138 to 54848 HEFNER 4 138 CKT 1 | 222 | 81.5953 | 102.0561 | 84TH ST - TENNESSEE TAP 138KV | 54837 TENESTP4 138 to 54843 84TH ST4 138 CKT 1 | 1097 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 59.4454 | 103.8136 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1108 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 20.1847 | 102.8558 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1118 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 63.5579 | 102.4576 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 1120 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 19.2041 | 101.9555 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 1137 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 52.3543 | 101.1331 | HEFNER - LAKESIDE 138KV | 54848 HEFNER 4 138 to 54849 LAKESID4 138 CKT 1 | 1138 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 52.1173 | 103.1748 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1139 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 59.8798 | 102.152 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1144 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 17.7806 | 101.642 | DRAPER LAKE - POOST ROAD 138KV | 54933 DRAPER 4 138 to 54965 POSTRDT4 138 CKT 1 | 1147 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 41.5463 | 101.7225 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1155 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 18.9088 | 101.5174 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 1156 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 62.3276 | 101.1008 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1164 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 67.1301 | 100.5793 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1177 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 52.273 | 100.8176 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1180 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 31.9118 | 119.4967 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 930 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 31.8458 | 119.2589 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 933 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 18.0807 | 105.6462 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1066 | Solution Undetermined
10SP | OKGE | AEPW | BONANZA - BONANZA TAP 161KV | 55261 BONANZT5 161 to 53126 BONANZA5 161 CKT 1 | 177 | 101.562 | 101.9273 | AES - TARBY 161KV | 55262 AES 5 161 to 55264 TARBY 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 101.3147 | 105.0903 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 99.0941 | 127.9686 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 39 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 99.0941 | 127.9686 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 39 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 96.0646 | 122.4304 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 172 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 96.0646 | 122.4304 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 172 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 95.8778 | 104.9132 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 436 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 95.6972 | 104.7331 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 455 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 87.1262 | 121.7318 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 474 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 85.342 | 117.5336 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 554 | Solution Undetermined
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 94.1271 | 102.9134 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 625 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 93.9583 | 102.7465 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 645 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 59.698 | 124.6808 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 678 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 79.8215 | 111.6964 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 780 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 53.0211 | 117.7161 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 799 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 54.6448 | 118.2469 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 803 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 31.4521 | 121.2707 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 808 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 71.5328 | 127.4185 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 814 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 53.2699 | 115.2719 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 853 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 53.7333 | 113.6809 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 862 | Solution Undetermined
10SP | OKGE | OKGE | POOST ROAD - SE15TH 138KV | 54993 SE15TH 4 138 to 54965 POSTRDT4 138 CKT 1 | 191 | 50.0418 | 108.3503 | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 863 | May Limit Renewal Rights
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 78.207 | 107.6762 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 876 | Solution Undetermined
10SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 67.2562 | 104.864 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 889 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 18.1604 | 118.3791 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 890 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 52.3616 | 110.6931 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 919 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 71.8831 | 115.4932 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 921 | Solution Undetermined
10SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 52.1042 | 103.6705 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 953 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 19.2762 | 110.4536 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 971 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 85.7633 | 103.0908 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 975 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 69.3561 | 109.766 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 983 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 53.1716 | 102.1109 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 986 | May Limit Renewal Rights
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 55.2572 | 104.23 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 996 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 24.658 | 113.6249 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1018 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 24.607 | 113.3968 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1021 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 52.1422 | 111.2659 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1042 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 78.8769 | 101.916 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1052 | May Limit Renewal Rights
10SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 6.4899 | 107.2527 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1055 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 40.9021 | 105.1312 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 1057 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 53.2497 | 109.4846 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1059 | Solution Undetermined
10SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 67.9261 | 103.7393 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 1074 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 61.1921 | 105.868 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1090 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 47.412 | 103.9447 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1093 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 287 | 40.916 | 109.5389 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1094 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 69.2342 | 102.9968 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1094 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 40.9803 | 104.5009 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1101 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 64.4361 | 104.3234 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 1101 | Solution Undetermined
10SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 67.1419 | 102.9211 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 1102 | Solution Undetermined
10SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 61.0675 | 103.977 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1126 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 18.5269 | 102.2975 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1138 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 57.8075 | 103.2932 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1142 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 47.6454 | 103.6795 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1148 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 17.5745 | 101.5186 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 1155 | Solution Undetermined
10SP | OKGE | OKGE | HEFNER - TULSA 138KV | 54847 TULSA 4 138 to 54848 HEFNER 4 138 CKT 1 | 222 | 80.9743 | 100.9953 | 84TH ST - TENNESSEE TAP 138KV | 54837 TENESTP4 138 to 54843 84TH ST4 138 CKT 1 | 1158 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 62.1764 | 101.6976 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 1160 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 58.5198 | 101.9059 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1165 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 40.5542 | 101.242 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1170 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 49.6952 | 102.1542 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1170 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 17.0043 | 100.703 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 1181 | Solution Undetermined
10SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 72.3203 | 100.9389 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1182 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 68.1865 | 100.3717 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1185 | Solution Undetermined
10SP | OKGE | OMPA | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 287 | 47.0403 | 100.3566 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1190 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 44.55 | 100.6788 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1190 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 60.8821 | 100.2602 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1194 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 15.8339 | 100.0934 | DRAPER LAKE - POOST ROAD 138KV | 54933 DRAPER 4 138 to 54965 POSTRDT4 138 CKT 1 | 1196 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 71.6775 | 158.7997 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 118.686 | 158.7968 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 31.6609 | 116.8354 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 965 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 31.5953 | 116.592 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 968 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 36.2624 | 108.3784 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1006 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 44.544 | 104.7573 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1057 | Solution Undetermined
10WP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 30.716 | 101.7165 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1158 | Solution Undetermined
[11 empty] | Total Cost | 0

## Table 1a
Study Case | From Area | To Area | Monitored Branch Over 100% Rate B | Monitored Branch Over 100% Rate B | Rate <MVA> | BC % Loading | TC % Loading | Outaged Branch Causing Overload | Outaged Branch Causing Overload | ATC (MW) | Solution | Cost
04G | WERE | WERE | ATHENS SWITCHING STATION - COFFEY COUNTY NO. 4 VERNON 69KV | 57631 CC4VERN2 69 to 57623 ATHENS 2 69 CKT 1 | 45 | 104.4807 | 105.7617 | LACYGNE - WOLF CREEK 345KV | 56797 WOLFCRK7 345 to 57981 LACYGNE7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04G | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 118.5007 | 118.8464 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04G | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 102.6672 | 102.9224 | IATAN - ST JOE 345KV | 57982 IATAN 7 345 to 59199 ST JOE 3 345 CKT 1 | 0 | Rebuild 15.50-mile line (1192.5 kcmil 45/7 ACSR, 223 MVA, 245 MVA), Replace CTs and Wave Trap (2000 A.) | 5800000
04G | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 100.7079 | 100.8403 | CONCORDIA - EAST MANHATTAN 230KV | 56861 EMANHAT6 230 to 58758 CONCORD6 230 CKT 1 | 0 | See Previous Upgrade Specified
04G | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 100.6566 | 100.8037 | CONCORDIA 230/115KV TRANSFORMER | 58757 CONCORD3 115 to 58758 CONCORD6 230 CKT 1 | 0 | See Previous Upgrade Specified
04G | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 113.4655 | 113.8263 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04G | WERE | WERE | COFFEY COUNTY NO. 4 VERNON - GREEN 69KV | 57636 GREEN 2 69 to 57631 CC4VERN2 69 CKT 1 | 45 | 105.7467 | 107.0278 | LACYGNE - WOLF CREEK 345KV | 56797 WOLFCRK7 345 to 57981 LACYGNE7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04G | WERE | WERE | COFFEY COUNTY NO. 4 VERNON - GREEN 69KV | 57636 GREEN 2 69 to 57631 CC4VERN2 69 CKT 1 | 45 | 100.5435 | 101.0906 | ROSE HILL - WOLF CREEK 345KV | 56794 ROSEHIL7 345 to 56797 WOLFCRK7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04G | WERE | WERE | COFFEY COUNTY NO. 4 VERNON - GREEN 69KV | 57636 GREEN 2 69 to 57631 CC4VERN2 69 CKT 1 | 45 | 100.2507 | 100.7446 | BENTON - WOLF CREEK 345KV | 56791 BENTON 7 345 to 56797 WOLFCRK7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04G | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 111.3527 | 111.7131 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04SP | GRRD | GRRD | BRISTOW - KELLYVILLE 69KV | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 119.7607 | 120.4708 | MANFORD - SILVER CITY 69KV | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 0 | GRDA to Construct 138/69 KV Fisher Sub, tapping Keystone -- Silver City 138 KV T-line by 6/2005
04SP | SWPA | ENTR | BULL SHOALS - MIDWAY 161KV | 52660 BULL SH5 161 to 99825 5MIDWAY# 161 CKT 1 | 162 | 102.0335 | 102.2531 | INDEPENDENCE - MOOREFIELD 161KV | 99817 5ISES 1 161 to 99826 5MORFLD 161 CKT 1 | 0 | Replace disconnect switches, metering CTs and wave trap at Bull Shoals. | 150000
04SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 112.2195 | 112.601 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
04SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 109.6978 | 110.0692 | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
04SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 106.0875 | 106.4427 | SUB 382 - LARUSSEL - SUB 383 - MONETT 161KV | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
04SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 104.415 | 104.7802 | JASPER - LAMAR 69KV | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
04SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 101.9049 | 102.2296 | SUB 124 - AURORA H.T. - SUB 355 - AURORA WEST 69KV | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
04SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 335 | 102.9049 | 103.0777 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | Replace Farmington switch 8839 | 60000
04SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 132.3868 | 133.2241 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | Rebuild 12 miles with 2156MCM ACSR. Replace Chamber Springs wavetrap & reset relays. | 7200000
04SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 244 | 122.3263 | 122.842 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 118.6957 | 119.5398 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 100.2142 | 100.8617 | FLINT CREEK - GENTRY REC 161KV | 53139 FLINTCR5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SP | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 84 | 106.6162 | 106.6958 | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 0 | Add 3rd 161/69 KV Transformer | 1250000
04SP | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 84 | 106.9349 | 107.0149 | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 0 | See Previous Upgrade Specified
04SP | OMPA | AEPW | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 56204 OMDUNCN4 138 to 54157 COMMTAP4 138 CKT 1 | 117 | 105.7062 | 106.6745 | CORNVILLE - RUSH SPRINGS NATURAL GAS TAP 138KV | 54112 CORNVIL4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | Rebuild 17.81 miles of 266 ACSR with 795 ACSR | 6100000
04SP | AEPW | AEPW | DYESS - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53131 DYESS 5 161 CKT 1 | 313 | 100.9179 | 101.0027 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | Replace South Springdale Circuit Switcher & Jumpers | 60000
04SP | GRDA | GRDA | KINZIE 138/69KV TRANSFORMER | 54510 KINZEGR4 138 to 54513 KINZEGR2 69 CKT 1 | 56 | 112.2145 | 112.3645 | CENTRAL - STILLWATER 69KV | 54453 CENTRL 2 69 to 96845 2STILWTR 69 CKT 1 | 0 | Solution Undetermined
04SP | GRDA | GRDA | TAHLEQUAH 161/69KV TRANSFORMER CKT 1 | 54455 TAHLQH 5 161 to 54447 TAHLQH 2 69 CKT 1 | 78 | 107.5648 | 108.8961 | TAHLEQUAH 161/69KV TRANSFORMER CKT 2 | 54447 TAHLQH 2 69 to 54455 TAHLQH 5 161 CKT 2 | 0 | Add 3rd 161/69 KV Transformer | 1400000
04SP | GRDA | GRDA | TAHLEQUAH 161/69KV TRANSFORMER CKT 2 | 54455 TAHLQH 5 161 to 54447 TAHLQH 2 69 CKT 2 | 78 | 109.067 | 109.4934 | TAHLEQUAH 161/69KV TRANSFORMER CKT 1 | 54447 TAHLQH 2 69 to 54455 TAHLQH 5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SP | AEPW | AEPW | EAST CENTRAL HENRYETTA - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54049 EC.HEN-4 138 CKT 1 | 105 | 92.7795 | 105.0684 | KELCO - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54057 KELCO 4 138 CKT 1 | 705.0769 | Replace Okmulgee Wavetrap | 40000
04SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 99.4431 | 100.0887 | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 1035.1199 | See Previous Upgrade Specified
04SP | AEPW | AEPW | EAST CENTRAL HENRYETTA - WELEETKA 138KV | 54049 EC.HEN-4 138 to 54028 WELETK4 138 CKT 1 | 105 | 88.5803 | 100.8672 | KELCO - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54057 KELCO 4 138 CKT 1 | 1115.3048 | Replace Weleetka Wavetrap | 40000
04SP | AEPW | AEPW | ATOKA - ATOKA PUMP 69KV | 54004 ATOKA P2 69 to 54007 ATOKA--2 69 CKT 1 | 39 | 116.9999 | 117.0832 | LONE OAK - SOUTH MCALESTER TAP 138KV | 54022 LONEOAK4 138 to 54032 SMCALTP4 138 CKT 1 | 1200 | Invalid Contingency
04SP | AEPW | AEPW | MCALESTER - WELEETKA 69KV | 54024 MCALEST2 69 to 54029 WELEETK2 69 CKT 1 | 52 | 119.9831 | 120.3934 | LONE OAK - SOUTH MCALESTER TAP 138KV | 54022 LONEOAK4 138 to 54032 SMCALTP4 138 CKT 1 | 1200 | Invalid Contingency
04SP | SWPA | SWPA | SPRINGFIELD 161/69KV TRANSFORMER CKT 3 | 52694 SPRGFLD269.0 WND 1 SPF X3 1 | 25 | 100.2005 | 100.5317 | SPRINGFIELD 161/69KV TRANSFORMER CKT 1 | 52692 SPRGFLD5 161 to 52694 SPRGFLD269.0 to 52691 SPF X1 113.8 CKT 1 | 1200 | An outage of Springfield transformer #1 overloads transformer #3. If this situation were to occur, SWPA would open either the high or low side breaker on transformer #3 to remove the overload. This does not introduce any other overloads.
04SH | WERE | WERE | ANZIO - FORT JCT SWITCHING STATION 115KV | 57321 ANZIO 3 115 to 57328 FT JCT 3 115 CKT 1 | 92 | 100.1508 | 100.3527 | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57342 WJCCTY 3 115 to 57343 WJCCTYE3 115 CKT 1 | 0 | Solution Undetermined
04SH | WERE | WERE | ANZIO - FORT JCT SWITCHING STATION 115KV | 57321 ANZIO 3 115 to 57328 FT JCT 3 115 CKT 1 | 92 | 100.1472 | 100.349 | Multiple Outage Contingency: FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | Multiple Outage Contingency: 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 0 | May be relieved due to Westar Transmission Operating Directive 1217 Outage of the Fort JCT-West JCT City 115kV Line
04SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 105.9603 | 106.2001 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
04SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 103.5084 | 103.748 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
04SH | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 109.0465 | 109.7419 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SH | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 244 | 100.4446 | 100.9278 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
04SH | GRDA | GRDA | KINZIE 138/69KV TRANSFORMER | 54513 KINZEGR2 69 to 54510 KINZEGR4 138 CKT 1 | 56 | 108.9048 | 109.0936 | CENTRAL - STILLWATER 69KV | 54453 CENTRL 2 69 to 96845 2STILWTR 69 CKT 1 | 0 | Solution Undetermined
04SH | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57343 WJCCTYE3 115 to 57328 FT JCT 3 115 CKT 1 | 68 | 102.6653 | 102.9325 | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 1200 | Invalid Contingency
04FA | WERE | WERE | ATHENS SWITCHING STATION - COFFEY COUNTY NO. 4 VERNON 69KV | 57631 CC4VERN2 69 to 57623 ATHENS 2 69 CKT 1 | 45 | 107.6192 | 107.8365 | LACYGNE - WOLF CREEK 345KV | 56797 WOLFCRK7 345 to 57981 LACYGNE7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04FA | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 117.4023 | 117.7189 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04FA | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 112.3127 | 112.6434 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04FA | WERE | WERE | COFFEY COUNTY NO. 4 VERNON - GREEN 69KV | 57636 GREEN 2 69 to 57631 CC4VERN2 69 CKT 1 | 45 | 108.8919 | 109.1068 | LACYGNE - WOLF CREEK 345KV | 56797 WOLFCRK7 345 to 57981 LACYGNE7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1304 Overload of the Athens to Wolf Creek 69 kV Line
04FA | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 110.2001 | 110.5306 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 124.5347 | 124.7323 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 105.4587 | 105.7279 | IATAN - ST JOE 345KV | 57982 IATAN 7 345 to 59199 ST JOE 3 345 CKT 1 | 0 | See Previous Upgrade Specified
04WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 101.011 | 101.2366 | CONCORDIA - EAST MANHATTAN 230KV | 56861 EMANHAT6 230 to 58758 CONCORD6 230 CKT 1 | 0 | See Previous Upgrade Specified
04WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 100.9605 | 101.1866 | CONCORDIA 230/115KV TRANSFORMER | 58757 CONCORD3 115 to 58758 CONCORD6 230 CKT 1 | 0 | See Previous Upgrade Specified
04WP | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 121.2458 | 121.4524 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04WP | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 101.2154 | 101.4972 | IATAN - ST JOE 345KV | 57982 IATAN 7 345 to 59199 ST JOE 3 345 CKT 1 | 0 | Rebuild 15.15 mile line with 1192.5 kcmil ACSR. | 3200000
04WP | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 119.3634 | 119.5699 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
04WP | SWPA | SWPA | NORFORK 161/69KV TRANSFORMER CKT 1 | 52648 NORFORK5 161 WND 2 NFK X1 1 | 25 | 109.8084 | 109.8761 | NORFORK 161/69KV TRANSFORMER CKT 2 | 52648 NORFORK5 161 to 52650 NORFORK269.0 to 52651 NFK X2 113.8 CKT 1 | 0 | Replace Norfork Transformer | 1300000
04WP | SWPA | SWPA | NORFORK 161/69KV TRANSFORMER CKT 1 | 52650 NORFORK269.0 WND 1 NFK X1 1 | 25 | 109.0293 | 109.0945 | NORFORK 161/69KV TRANSFORMER CKT 2 | 52648 NORFORK5 161 to 52650 NORFORK269.0 to 52651 NFK X2 113.8 CKT 1 | 0 | See Previous Upgrade Specified
04WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 100.4638 | 100.7595 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | Tear down double circuit, build single circuit with 1192.5 ACSR. | 7800000
04WP | WERE | WERE | EL PASO - GILL ENERGY CENTER SOUTH 138KV | 57039 ELPASO 4 138 to 57046 GILL S 4 138 CKT 1 | 210 | 108.5813 | 108.8353 | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV | 57040 EVANS N4 138 to 57041 EVANS S4 138 CKT 1 | 1200 | Invalid Contingency
05AP | AEPW | CELE | INTERNATIONAL PAPER - WALLACE LAKE 138KV | 53461 WALLAKE4 138 to 50090 IPAPER 4 138 CKT 1 | 236 | 100.2983 | 101.6457 | DOLET HILLS 345/230KV TRANSFORMER | 50045 DOLHILL7 345 to 50046 DOLHILL6 230 CKT 1 | 0 | May be relieved by Dolet Hills Operating Guide
05AP | AEPW | AEPW | SOUTH SHREVEPORT - WALLACE LAKE 138KV | 53446 S SHV 4 138 to 53461 WALLAKE4 138 CKT 1 | 210 | 103.5951 | 104.9024 | DOLET HILLS 345/230KV TRANSFORMER | 50045 DOLHILL7 345 to 50046 DOLHILL6 230 CKT 1 | 0 | May be relieved by Dolet Hills Operating Guide
05G | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 118.3568 | 118.4866 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05G | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 113.063 | 113.1986 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05G | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 110.8862 | 111.0216 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05G | WERE | WERE | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JCT (SOUTH) 115KV | 57372 PHILIPS3 115 to 57374 SPHILPJ3 115 CKT 1 | 160 | 101.3986 | 101.5851 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | Rebuild 0.88 miles and reconductor with 1192.5 ACSR. | 417200
05G | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 109.4566 | 109.6565 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05G | WERE | WERE | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57343 WJCCTYE3 115 to 57342 WJCCTY 3 115 CKT 1 | 141 | 100.008 | 100.1209 | JEFFREY ENERGY CENTER - SUMMIT 345KV | 56766 JEC N 7 345 to 56773 SUMMIT 7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 402 Outage of the Jeffrey Energy Center to Summit 345 kV Line
05G | WERE | WERE | EL PASO - GILL ENERGY CENTER SOUTH 138KV | 57039 ELPASO 4 138 to 57046 GILL S 4 138 CKT 1 | 210 | 125.0947 | 125.2507 | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV | 57040 EVANS N4 138 to 57041 EVANS S4 138 CKT 1 | 1200 | Invalid Contingency
05G | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57343 WJCCTYE3 115 to 57328 FT JCT 3 115 CKT 1 | 68 | 104.8121 | 104.9402 | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 1200 | Invalid Contingency
05SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 152.6895 | 152.8014 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 147.8016 | 147.9723 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 133.5397 | 133.6375 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 129.2755 | 129.4248 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 112.7228 | 113.0773 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
05SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 108.9382 | 109.2865 | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
05SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 107.3321 | 107.6239 | SUB 382 - LARUSSEL - SUB 383 - MONETT 161KV | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
05SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 103.6568 | 104.0031 | JASPER - LAMAR 69KV | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
05SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 101.9003 | 102.1912 | SUB 124 - AURORA H.T. - SUB 355 - AURORA WEST 69KV | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
05SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 101.2727 | 101.4264 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 100.2918 | 100.4466 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 101.3604 | 101.5176 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | Rebuild 10.24 miles with 2156 ACSR, replace Chamber Springs wavetrap, & replace Farmington AECC bus. | 6400000
05SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 137.9994 | 138.8454 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 127.2473 | 127.7733 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 123.6495 | 124.503 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 104.6751 | 105.3335 | FLINT CREEK - GENTRY REC 161KV | 53139 FLINTCR5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 103.8508 | 104.5095 | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 84 | 107.0107 | 107.0801 | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 0 | See Previous Upgrade Specified
05SP | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 84 | 107.3275 | 107.3973 | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 0 | See Previous Upgrade Specified
05SP | OMPA | AEPW | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 56204 OMDUNCN4 138 to 54157 COMMTAP4 138 CKT 1 | 117 | 109.7694 | 110.6415 | CORNVILLE - RUSH SPRINGS NATURAL GAS TAP 138KV | 54112 CORNVIL4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
05SP | OMPA | AEPW | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 56204 OMDUNCN4 138 to 54157 COMMTAP4 138 CKT 1 | 117 | 100.1623 | 101.0329 | RUSH SPRINGS NATURAL GAS TAP - RUSH SPRINGS TAP 138KV | 54154 RUSHSPT4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
05SP | AEPW | AEPW | DYESS - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53131 DYESS 5 161 CKT 1 | 313 | 104.8129 | 104.8859 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57309 WEMPORI3 115 to 57301 EAST ST3 115 CKT 1 | 92 | 108.4841 | 108.619 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
05SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 101.7346 | 101.8427 | LOWELL - TONTITOWN 161KV | 53144 LOWELL 5 161 to 53170 TONTITN5 161 CKT 1 | 0 | Rebuild 1.09 miles of 2-397.5 ACSR with 2156 ACSR. Replace Flint Creek wavetrap & jumpers | 450000
05SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 143.9578 | 144.0692 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 139.3217 | 139.4915 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 126.0237 | 126.1212 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 121.9117 | 122.0603 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | GRDA | GRDA | KINZIE 138/69KV TRANSFORMER | 54510 KINZEGR4 138 to 54513 KINZEGR2 69 CKT 1 | 56 | 116.405 | 116.5676 | CENTRAL - STILLWATER 69KV | 54453 CENTRL 2 69 to 96845 2STILWTR 69 CKT 1 | 0 | Solution Undetermined
05SP | WERE | WERE | LAWRENCE HILL 230/115KV TRANSFORMER | 56853 LAWHILL6 230 WND 1 LAWHL29X 1 | 308 | 107.193 | 107.2736 | LAWRENCE HILL - MIDLAND JCT 230KV CKT 1 | 56853 LAWHILL6 230 to 56855 MIDLAND6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 901 Outage of the Lawrence Hill-Midland JCT 230kV Line
05SP | WERE | WERE | LAWRENCE HILL 230/115KV TRANSFORMER | 57250 LWRNCHL3 115 WND 2 LAWHL29X 1 | 308 | 105.2471 | 105.3279 | LAWRENCE HILL - MIDLAND JCT 230KV CKT 1 | 56853 LAWHILL6 230 to 56855 MIDLAND6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 901 Outage of the Lawrence Hill-Midland JCT 230kV Line
05SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 129.9402 | 130.051 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 125.7908 | 125.9588 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 113.4738 | 113.5706 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 109.8447 | 109.9914 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 132.1608 | 132.2716 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 128.0543 | 128.2228 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 115.4804 | 115.5769 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 111.8484 | 111.9956 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05SP | AEPW | AEPW | BLUE CIRCLE - CATOOSA 69KV | 53806 BCIRCLE2 69 to 53811 CATOOSA2 69 CKT 1 | 72 | 101.8954 | 102.1563 | LYNN LANE TAP - LYNN LANE WEST TAP 138KV | 53782 LLAN WT4 138 to 53816 LLANETP4 138 CKT 1 | 1200 | Invalid Contingency
05SP | AEPW | AEPW | MCALESTER - WELEETKA 69KV | 54024 MCALEST2 69 to 54029 WELEETK2 69 CKT 1 | 52 | 127.0412 | 127.4195 | LONE OAK - SOUTH MCALESTER TAP 138KV | 54022 LONEOAK4 138 to 54032 SMCALTP4 138 CKT 1 | 1200 | Invalid Contingency
05SH | WERE | WERE | ANZIO - FORT JCT SWITCHING STATION 115KV | 57321 ANZIO 3 115 to 57328 FT JCT 3 115 CKT 1 | 92 | 103.0172 | 103.1868 | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57342 WJCCTY 3 115 to 57343 WJCCTYE3 115 CKT 1 | 0 | Solution Undetermined
05SH | WERE | WERE | ANZIO - FORT JCT SWITCHING STATION 115KV | 57321 ANZIO 3 115 to 57328 FT JCT 3 115 CKT 1 | 92 | 103.0122 | 103.1817 | Multiple Outage Contingency: FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | Multiple Outage Contingency: 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 0 | May be relieved due to Westar Transmission Operating Directive 1217 Outage of the Fort JCT-West JCT City 115kV Line
05SH | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 147.7527 | 147.8918 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 129.2285 | 129.3501 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 110.4321 | 110.6621 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 107.4866 | 107.7143 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 109.7852 | 110.0135 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SH | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52690 CARTHG 269.0 WND 1 CRG X2 1 | 84 | 106.6756 | 106.9012 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05SH | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 115.6235 | 116.3204 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SH | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 244 | 106.5969 | 107.0796 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SH | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 244 | 103.9489 | 104.6544 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05SH | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 84 | 100.2153 | 100.3878 | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 0 | See Previous Upgrade Specified
05SH | GRDA | GRDA | CLAREMORE 161/69KV TRANSFORMER CKT 2 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 2 | 84 | 100.5104 | 100.6837 | CLAREMORE 161/69KV TRANSFORMER CKT 1 | 54451 CLARMR 5 161 to 54479 CLARMR 2 69 CKT 1 | 0 | See Previous Upgrade Specified
05SH | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57309 WEMPORI3 115 to 57301 EAST ST3 115 CKT 1 | 92 | 108.9607 | 109.1991 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
05SH | WERE | WERE | EXIDE JCT - SUMMIT 115KV | 57381 SUMMIT 3 115 to 57368 EXIDE J3 115 CKT 1 | 196 | 105.4933 | 105.562 | NORTHVIEW - SUMMIT 115KV | 57371 NORTHVW3 115 to 57381 SUMMIT 3 115 CKT 1 | 0 | Rebuild and reconductor 4.94 miles with 1192 ACSR. | 1100000
05SH | WERE | WERE | EXIDE JCT - SUMMIT 115KV | 57381 SUMMIT 3 115 to 57368 EXIDE J3 115 CKT 1 | 196 | 100.9694 | 101.2242 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05SH | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 140.6785 | 140.818 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 123.1479 | 123.2699 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 129.4684 | 129.6097 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 113.0589 | 113.1823 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 131.322 | 131.4619 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 114.7091 | 114.8313 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05SH | WERE | WERE | TECUMSEH HILL 161/115KV TRANSFORMER | 56920 TECHILL5 161 WND 1 1 | 69 | 100.2422 | 100.3413 | HOYT - HOYT HTI SWITCHING JCT 115KV CKT 1 | 57163 HOYT 3 115 to 57165 HTI JCT3 115 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 632 Overload of the Tecumseh Hill 161/115kV Transformer
05SH | WERE | WERE | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57343 WJCCTYE3 115 to 57342 WJCCTY 3 115 CKT 1 | 141 | 100.8718 | 101.1114 | JEFFREY ENERGY CENTER - SUMMIT 345KV | 56766 JEC N 7 345 to 56773 SUMMIT 7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 402 Outage of the Jeffrey Energy Center to Summit 345 kV Line
05SH | WERE | WERE | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57343 WJCCTYE3 115 to 57342 WJCCTY 3 115 CKT 1 | 141 | 100.6633 | 100.8999 | SUMMIT 345/230KV TRANSFORMER CKT 1 | 56773 SUMMIT 7 345 to 56873 SUMMIT 6 230 to 56813 SUMMIT 114.4 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 617 Outage of the Summit 345/230kV Transformer
05SH | AEPW | AEPW | EAST CENTRAL HENRYETTA - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54049 EC.HEN-4 138 CKT 1 | 105 | 87.8832 | 105.0982 | KELCO - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54057 KELCO 4 138 CKT 1 | 844.6211 | See Previous Upgrade Specified
05SH | AEPW | AEPW | EAST CENTRAL HENRYETTA - WELEETKA 138KV | 54049 EC.HEN-4 138 to 54028 WELETK4 138 CKT 1 | 105 | 84.1328 | 101.3502 | KELCO - OKMULGEE 138KV | 54023 OKMULGE4 138 to 54057 KELCO 4 138 CKT 1 | 1105.8954 | See Previous Upgrade Specified
05SH | SWPA | AECI | DONIPHAN 161/69KV TRANSFORMER CKT 1 | 52640 DONIPHN5 161 to 97201 2DONIPH 69 CKT 1 | 18.75 | 151.5073 | 151.7276 | DONIPHAN 161/69KV TRANSFORMER CKT 2 | 52640 DONIPHN5 161 to 97201 2DONIPH 69 CKT 2 | 1200 | Local area problem. Transformer is owned by AECI.
05SH | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57343 WJCCTYE3 115 to 57328 FT JCT 3 115 CKT 1 | 68 | 104.2758 | 104.4957 | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 1200 | Invalid Contingency
05FA | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57151 AUBURN 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 137.2796 | 137.4624 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57151 AUBURN 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 125.6496 | 125.7685 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57151 AUBURN 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 120.0166 | 120.1765 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 109.8748 | 109.9789 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | GRRD | GRRD | BRISTOW - KELLYVILLE 69KV | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 101.2262 | 101.3505 | MANFORD - SILVER CITY 69KV | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 0 | GRDA to Construct 138/69 KV Fisher Sub, tapping Keystone -- Silver City 138 KV T-line by 6/2005
05FA | EMDE | SWPA | CARTHAGE - SUB 109 - ATLAS JCT. 161KV | 59466 ATL109 5 161 to 52688 CARTHAG5 161 CKT 1 | 167 | 111.9745 | 112.4014 | SUB 292 - TIPTON FORD - SUB 389 - JOPLIN SOUTHWEST 161KV | 59472 TIP292 5 161 to 59483 JOP389 5 161 CKT 1 | 0 | Replace 600 Amp disconnect switches | 60000
05FA | EMDE | SWPA | CARTHAGE - SUB 109 - ATLAS JCT. 161KV | 59466 ATL109 5 161 to 52688 CARTHAG5 161 CKT 1 | 167 | 101.9824 | 102.3466 | SUB 349 - ASBURY - SUB 421 - PURCELL SOUTHWEST 161KV | 59476 ASB349 5 161 to 59491 PUR421 5 161 CKT 1 | 0 | See Previous Upgrade Specified
05FA | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 100.8693 | 101.0665 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05FA | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 100.2498 | 100.4456 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
05FA | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 111.8219 | 112.0078 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05FA | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 106.2042 | 106.3986 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05FA | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57301 EAST ST3 115 to 57309 WEMPORI3 115 CKT 1 | 92 | 100.5693 | 100.7924 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
05FA | WERE | WERE | EXIDE JCT - NORTH AMERICAN PHILIPS 115KV | 57368 EXIDE J3 115 to 57372 PHILIPS3 115 CKT 1 | 196 | 102.2528 | 102.4649 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | Rebuild and reconductor 0.34 miles with 1192 ACSR. | 95200
05FA | WERE | WERE | EXIDE JCT - SUMMIT 115KV | 57381 SUMMIT 3 115 to 57368 EXIDE J3 115 CKT 1 | 196 | 107.4521 | 107.6668 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05FA | WERE | WERE | EXIDE JCT - SUMMIT 115KV | 57381 SUMMIT 3 115 to 57368 EXIDE J3 115 CKT 1 | 196 | 101.1912 | 101.2568 | NORTHVIEW - SUMMIT 115KV | 57371 NORTHVW3 115 to 57381 SUMMIT 3 115 CKT 1 | 0 | See Previous Upgrade Specified
05FA | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 | 68 | 100.5271 | 100.7188 | JEFFREY ENERGY CENTER - SUMMIT 345KV | 56766 JEC N 7 345 to 56773 SUMMIT 7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 402 Outage of the Jeffrey Energy Center to Summit 345 kV Line
05FA | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 | 68 | 100.2163 | 100.4048 | SUMMIT 345/230KV TRANSFORMER CKT 1 | 56773 SUMMIT 7 345 to 56873 SUMMIT 6 230 to 56813 SUMMIT 114.4 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 617 Outage of the Summit 345/230kV Transformer
05FA | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 131.5447 | 131.7266 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 119.8256 | 119.9441 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 115.0939 | 115.2532 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 104.8435 | 104.9472 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 104.0997 | 104.2939 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05FA | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 122.3827 | 122.5632 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 110.5472 | 110.6648 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 106.864 | 107.0217 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JCT (SOUTH) 115KV | 57372 PHILIPS3 115 to 57374 SPHILPJ3 115 CKT 1 | 160 | 113.5114 | 113.9525 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05FA | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 122.5213 | 122.9973 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05FA | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 2 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 2 | 92 | 106.9258 | 107.3415 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05FA | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 124.057 | 124.2376 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 112.1545 | 112.2724 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05FA | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 108.3451 | 108.5029 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
05FA | EMDE | EMDE | SUB 110 - ORONOGO JCT. - SUB 432 - JOPLIN OAKLAND NORTH 161KV | 59467 ORO110 5 161 to 59494 OAK432 5 161 CKT 1 | 214 | 101.3483 | 101.6487 | SUB 292 - TIPTON FORD - SUB 389 - JOPLIN SOUTHWEST 161KV | 59472 TIP292 5 161 to 59483 JOP389 5 161 CKT 1 | 0 | Reconstruct and replace 1.4 miles of 556 ACSR with Bundled 556 ACSR. | 800000
05FA | WERE | WERE | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57343 WJCCTYE3 115 to 57342 WJCCTY 3 115 CKT 1 | 141 | 105.8524 | 106.0544 | JEFFREY ENERGY CENTER - SUMMIT 345KV | 56766 JEC N 7 345 to 56773 SUMMIT 7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 402 Outage of the Jeffrey Energy Center to Summit 345 kV Line
05FA | WERE | WERE | WEST JCT CITY - WEST JCT CITY JCT (EAST) 115KV | 57343 WJCCTYE3 115 to 57342 WJCCTY 3 115 CKT 1 | 141 | 105.5246 | 105.7231 | SUMMIT 345/230KV TRANSFORMER CKT 1 | 56773 SUMMIT 7 345 to 56873 SUMMIT 6 230 to 56813 SUMMIT 114.4 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 617 Outage of the Summit 345/230kV Transformer
05FA | EMDE | SWPA | CARTHAGE - SUB 109 - ATLAS JCT. 161KV | 59466 ATL109 5 161 to 52688 CARTHAG5 161 CKT 1 | 167 | 99.7636 | 100.1565 | SUB 395 - CARTHAGE SOUTHWEST - SUB 421 - PURCELL SOUTHWEST 161KV | 59485 CAR395 5 161 to 59491 PUR421 5 161 CKT 1 | 722.0644 | See Previous Upgrade Specified
05FA | WERE | WERE | EL PASO - GILL ENERGY CENTER SOUTH 138KV | 57039 ELPASO 4 138 to 57046 GILL S 4 138 CKT 1 | 210 | 115.5366 | 115.7261 | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV | 57040 EVANS N4 138 to 57041 EVANS S4 138 CKT 1 | 1200 | Invalid Contingency
05WP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57151 AUBURN 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 110.2832 | 110.408 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05WP | GRRD | GRRD | BRISTOW - KELLYVILLE 69KV | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 100.3131 | 100.4908 | MANFORD - SILVER CITY 69KV | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 0 | GRDA to Construct 138/69 KV Fisher Sub, tapping Keystone -- Silver City 138 KV T-line by 6/2005
05WP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 275 | 103.1067 | 103.6485 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
05WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 112.2829 | 112.5299 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05WP | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 108.1486 | 108.4053 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05WP | AEPW | AEPW | JERICHO 115/69KV TRANSFORMER | 54276 JERICHO3 115 WND 2 1 | 46 | 107.2874 | 108.0504 | AMOCO TAP - CHILDRESS 69KV CKT 1 | 54287 AMOCOTP269.0 to 54289 CHLDR2WT69.0 CKT 1 | 0 | Solution Undetermined
05WP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 105.2513 | 105.3816 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
05WP | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 106.2104 | 106.4665 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
05WP | SWPA | SWPA | NORFORK 161/69KV TRANSFORMER CKT 1 | 52648 NORFORK5 161 WND 2 NFK X1 1 | 25 | 110.3021 | 110.3696 | NORFORK 161/69KV TRANSFORMER CKT 2 | 52648 NORFORK5 161 to 52650 NORFORK269.0 to 52651 NFK X2 113.8 CKT 1 | 0 | See Previous Upgrade Specified
05WP | WERE | WERE | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JCT (SOUTH) 115KV | 57372 PHILIPS3 115 to 57374 SPHILPJ3 115 CKT 1 | 160 | 105.4654 | 106.0118 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 113.8472 | 114.4368 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
05WP | WERE | WERE | EL PASO - GILL ENERGY CENTER SOUTH 138KV | 57039 ELPASO 4 138 to 57046 GILL S 4 138 CKT 1 | 210 | 103.3751 | 103.5698 | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV | 57040 EVANS N4 138 to 57041 EVANS S4 138 CKT 1 | 1200 | Invalid Contingency
05WP | AEPW | AEPW | JERICHO 115/69KV TRANSFORMER | 54276 JERICHO3 115 WND 2 1 | 46 | 107.2654 | 108.0255 | CHILDRESS 138/69KV TRANSFORMER CKT 1 | 54289 CHLDR2WT69.0 to 54290 CHILD4WT 138 to 54305 WC2TERT 12.5 CKT 1 | 1200 | Invalid Contingency
07SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 172.1621 | 172.2828 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 155.0746 | 155.289 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 150.5607 | 150.6662 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 135.6328 | 135.8203 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | GRRD | GRRD | BRISTOW - KELLYVILLE 69KV | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 131.201 | 131.495 | MANFORD - SILVER CITY 69KV | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 0 | GRDA to Construct 138/69 KV Fisher Sub, tapping Keystone -- Silver City 138 KV T-line by 6/2005
07SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 113.3566 | 113.6619 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 109.5358 | 109.7997 | SUB 382 - LARUSSEL - SUB 383 - MONETT 161KV | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 108.6758 | 108.9799 | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 103.0938 | 103.3928 | JASPER - LAMAR 69KV | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 102.1919 | 102.4427 | SUB 124 - AURORA H.T. - SUB 355 - AURORA WEST 69KV | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 106.2279 | 106.3605 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
07SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 104.7282 | 104.8619 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
07SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 105.585 | 105.7191 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
07SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52690 CARTHG 269.0 WND 1 CRG X2 1 | 84 | 104.0506 | 104.1858 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
07SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 108.7882 | 108.9479 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 101.1977 | 101.6403 | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 145.8185 | 146.7008 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 133.7874 | 134.3271 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 130.0556 | 130.9475 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 110.1002 | 110.783 | FLINT CREEK - GENTRY REC 161KV | 53139 FLINTCR5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 109.1339 | 109.8175 | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | OMPA | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 54157 COMMTAP4 138 to 56204 OMDUNCN4 138 CKT 1 | 117 | 112.5212 | 113.4122 | CORNVILLE - RUSH SPRINGS NATURAL GAS TAP 138KV | 54112 CORNVIL4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | OMPA | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 54157 COMMTAP4 138 to 56204 OMDUNCN4 138 CKT 1 | 117 | 102.8988 | 103.7937 | RUSH SPRINGS NATURAL GAS TAP - RUSH SPRINGS TAP 138KV | 54154 RUSHSPT4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | DYESS - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53131 DYESS 5 161 CKT 1 | 313 | 113.0345 | 113.1043 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | Limits Renewal Rights
07SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 103.0368 | 103.1274 | LOWELL - TONTITOWN 161KV | 53144 LOWELL 5 161 to 53170 TONTITN5 161 CKT 1 | 0 | Limits Renewal Rights and May be a problem in the 06SP
07SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 100.5365 | 100.6264 | LOWELL - ROGERS 161KV | 53144 LOWELL 5 161 to 53152 ROGERS 5 161 CKT 1 | 0 | Limits Renewal Rights and May be a problem in the 06SP
07SP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57309 WEMPORI3 115 to 57301 EAST ST3 115 CKT 1 | 92 | 105.7015 | 105.82 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
07SP | AEPW | AEPW | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 313 | 100.258 | 100.4351 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | Limits Renewal Rights
07SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 105.9416 | 106.0327 | LOWELL - TONTITOWN 161KV | 53144 LOWELL 5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 103.4482 | 103.5381 | LOWELL - ROGERS 161KV | 53144 LOWELL 5 161 to 53152 ROGERS 5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 102.2495 | 102.3016 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 162.5449 | 162.6653 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57167 KEENE 3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 145.7502 | 145.9771 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 142.2843 | 142.3896 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 127.5545 | 127.7535 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | GRDA | GRDA | KINZIE 138/69KV TRANSFORMER | 54510 KINZEGR4 138 to 54513 KINZEGR2 69 CKT 1 | 56 | 126.2645 | 126.524 | CENTRAL - STILLWATER 69KV | 54453 CENTRL 2 69 to 96845 2STILWTR 69 CKT 1 | 0 | Solution Undetermined
07SP | SPS | SPS | KRESS INTERCHANGE 115/69KV TRANSFORMER CKT 1 | 51316 KRESS3 115 to 51315 KRESS2 69 CKT 1 | 44 | 153.6232 | 153.8493 | KRESS INTERCHANGE 115/69KV TRANSFORMER CKT 2 | 51315 KRESS2 69 to 51316 KRESS3 115 CKT 2 | 0 | May be relieved due to Xcel Energy Transmission Operating Directive for Loss of the Kress 115/69 kV autotransformer
07SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57335 MCDOWEL3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 147.0759 | 147.1964 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 131.236 | 131.4921 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57335 MCDOWEL3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 128.4602 | 128.5655 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 114.6015 | 114.8252 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | AEPW | AEPW | SNYDER - TIPTON & HEADERICK 69KV | 54125 HEADRIK2 69 to 54138 SNYDER-2 69 CKT 1 | 53 | 101.4155 | 101.9272 | HOBART JCT - TAMARAC TAP 138KV | 54126 HOB-JCT4 138 to 54158 TAMARTP4 138 CKT 1 | 0 | Limits Renewal Rights and May be a problem in the 06SP
07SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 149.4517 | 149.5711 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 133.5452 | 133.7872 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 130.6016 | 130.706 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
07SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 116.6491 | 116.8605 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
07SP | AEPW | AEPW | BLUE CIRCLE - CATOOSA 69KV | 53806 BCIRCLE2 69 to 53811 CATOOSA2 69 CKT 1 | 72 | 104.7563 | 105.0389 | LYNN LANE TAP - LYNN LANE WEST TAP 138KV | 53782 LLAN WT4 138 to 53816 LLANETP4 138 CKT 1 | 1200 | Invalid Contingency
07SP | AEPW | AEPW | MCALESTER - WELEETKA 69KV | 54024 MCALEST2 69 to 54029 WELEETK2 69 CKT 1 | 52 | 134.2412 | 134.4697 | LONE OAK - SOUTH MCALESTER TAP 138KV | 54022 LONEOAK4 138 to 54032 SMCALTP4 138 CKT 1 | 1200 | Invalid Contingency
07WP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 43 | 104.8407 | 105.1985 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07WP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 43 | 100.311 | 100.6438 | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
07WP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 275 | 106.2806 | 107.0013 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
07WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 108.5235 | 108.6063 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
07WP | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 102.7234 | 102.8089 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
07WP | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 100.5755 | 100.6609 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
07WP | WERE | WERE | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JCT (SOUTH) 115KV | 57372 PHILIPS3 115 to 57374 SPHILPJ3 115 CKT 1 | 160 | 111.2832 | 111.7693 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
07WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 120.1261 | 120.6504 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
07WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 2 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 2 | 92 | 104.8178 | 105.2757 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
07WP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57301 EAST ST3 115 to 57309 WEMPORI3 115 CKT 1 | 92 | 99.9152 | 100.1435 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 445.7293 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
07WP | WERE | WERE | EL PASO - GILL ENERGY CENTER SOUTH 138KV | 57039 ELPASO 4 138 to 57046 GILL S 4 138 CKT 1 | 210 | 105.6178 | 105.877 | EVANS ENERGY CENTER NORTH - EVANS ENERGY CENTER SOUTH 138KV | 57040 EVANS N4 138 to 57041 EVANS S4 138 CKT 1 | 1200 | Invalid Contingency
10SP | AEPW | AEPW | ANTLERS TAP - VALLEY TIMBER 69KV | 54019 VALYTIM2 69 to 54041 ANTLTAP2 69 CKT 1 | 48 | 101.2238 | 101.6678 | ALLEN NATURAL GAS TAP - TUPELO 138KV | 52800 TUPELO 4 138 to 54006 ALLENGT4 138 CKT 1 | 0 | Possible Invalid Contingency
10SP | AEPW | AEPW | ATOKA 138/69KV TRANSFORMER | 54007 ATOKA--269.0 WND 1 1 | 36 | 105.7499 | 105.8122 | ALLEN NATURAL GAS TAP - TUPELO 138KV | 52800 TUPELO 4 138 to 54006 ALLENGT4 138 CKT 1 | 0 | Possible Invalid Contingency
10SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 221.6486 | 221.7721 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 1 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 1 | 68 | 180.5945 | 180.7728 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 193.8228 | 193.9308 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | AUBURN ROAD - KEENE 115KV CKT 2 | 57167 KEENE 3 115 to 57151 AUBURN 3 115 CKT 2 | 92 | 157.941 | 158.0969 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | GRRD | GRRD | BRISTOW - KELLYVILLE 69KV | 96901 2KELYVIL 69 to 96889 2BRISTOW 69 CKT 1 | 51 | 145.174 | 145.448 | MANFORD - SILVER CITY 69KV | 96936 2MANFORD 69 to 96943 2SILVCTY 69 CKT 1 | 0 | GRDA to Construct 138/69 KV Fisher Sub, tapping Keystone -- Silver City 138 KV T-line by 6/2005
10SP | SWPA | SPRM | BROOKLINE - SPRINGFIELD 161KV | 52692 SPRGFLD5 161 to 59969 BRKLNE 5 161 CKT 1 | 323 | 103.8995 | 103.968 | BROOKLINE - JCT 161KV | 59955 JUNCTN 5 161 to 59969 BRKLNE 5 161 CKT 1 | 0 | Limits Renewal Rights
10SP | SWPA | AECI | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 47 | 104.9571 | 105.0661 | 2MILO - 2CLARK 69KV CKT 1 | 96654 2MILO 69 to 96802 2CLARK 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 118.0388 | 118.3603 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 115.0522 | 115.3008 | SUB 382 - LARUSSEL - SUB 383 - MONETT 161KV | 59479 LAR382 5 161 to 59480 MON383 5 161 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 112.8143 | 113.118 | CARTHAGE - JASPER 69KV | 52690 CARTHG 2 69 to 96649 2JASPER 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 106.8048 | 107.1037 | JASPER - LAMAR 69KV | 96649 2JASPER 69 to 96651 2LAMAR 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | AECI | CARTHAGE - REEDS 69KV | 52690 CARTHG 2 69 to 96751 2REEDS 69 CKT 1 | 36 | 106.286 | 106.5363 | SUB 124 - AURORA H.T. - SUB 355 - AURORA WEST 69KV | 59537 AUR124 2 69 to 59578 AUR355 2 69 CKT 1 | 0 | AECI third party line. No SWPA upgrades required.
10SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 WND 2 CRG X1 1 | 84 | 111.335 | 111.4658 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
10SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52690 CARTHG 269.0 WND 1 CRG X1 1 | 84 | 109.9227 | 110.0548 | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52689 CRG X2 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
10SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52688 CARTHAG5 161 WND 2 CRG X2 1 | 84 | 110.6496 | 110.7795 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
10SP | SWPA | SWPA | CARTHAGE 161/69KV TRANSFORMER CKT 2 | 52690 CARTHG 269.0 WND 1 CRG X2 1 | 84 | 109.2023 | 109.3335 | CARTHAGE 161/69KV TRANSFORMER CKT 1 | 52688 CARTHAG5 161 to 52690 CARTHG 269.0 to 52687 CRG X1 113.8 CKT 1 | 0 | Transformer owned by City of Carthage and AECI.
10SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 125.5491 | 125.7128 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 114.4222 | 114.8675 | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 107.5494 | 107.71 | EAST FAYETTEVILLE REC - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53193 EFAYTVL5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 106.9482 | 107.1913 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53195 FARMGTN5 161 to 53154 CHAMSPR5 161 CKT 1 | 353 | 105.4135 | 105.7131 | FLINT CREEK - GENTRY REC 161KV | 53139 FLINTCR5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - FLINT CREEK 161KV | 53154 CHAMSPR5 161 to 53139 FLINTCR5 161 CKT 1 | 335 | 107.7744 | 107.8817 | CHAMBER SPRINGS 345/161KV TRANSFORMER | 53154 CHAMSPR5 161 to 53155 CHAMSPR7 345 to 53120 CHAMSPR113.8 CKT 1 | 0 | Limits Renewal Rights
10SP | AEPW | AEPW | CHAMBER SPRINGS - FLINT CREEK 161KV | 53154 CHAMSPR5 161 to 53139 FLINTCR5 161 CKT 1 | 335 | 107.7731 | 107.8804 | CHAMBER SPRINGS - CLARKSVILLE 345KV | 53155 CHAMSPR7 345 to 53756 CLARKSV7 345 CKT 1 | 0 | Limits Renewal Rights
10SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 166.2418 | 167.1591 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 149.8959 | 150.4372 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 146.4557 | 147.3785 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 123.5333 | 124.2378 | FLINT CREEK - GENTRY REC 161KV | 53139 FLINTCR5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 244 | 122.1862 | 122.8912 | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | WERE | WERE | CHASE - WHITE JCT 69KV | 57605 WHITE J269.0 to 57588 CHASE 269.0 CKT 1 | 43 | 103.2658 | 103.423 | WEAVER 138/69KV TRANSFORMER CKT 1 | 56991 WEAVER 4 138 to 57604 WEAVER 269.0 to 57083 WEAVER 113.2 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 634 Outage of the Weaver 138-69kV Transformer
10SP | OMPA | AEPW | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 56204 OMDUNCN4 138 to 54157 COMMTAP4 138 CKT 1 | 117 | 121.1464 | 122.0974 | CORNVILLE - RUSH SPRINGS NATURAL GAS TAP 138KV | 54112 CORNVIL4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | OMPA | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 54157 COMMTAP4 138 to 56204 OMDUNCN4 138 CKT 1 | 117 | 111.239 | 112.1951 | RUSH SPRINGS NATURAL GAS TAP - RUSH SPRINGS TAP 138KV | 54154 RUSHSPT4 138 to 54155 RUSHNGT4 138 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | OMPA | COMANCHE TAP - OMPA-DUNCAN 840 138KV | 54157 COMMTAP4 138 to 56204 OMDUNCN4 138 CKT 1 | 117 | 106.9198 | 107.8732 | OMPA-MARLOW - RUSH SPRINGS TAP 138KV | 54154 RUSHSPT4 138 to 56207 OMMARLO4 138 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | DYESS - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53131 DYESS 5 161 CKT 1 | 313 | 133.192 | 133.3043 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | Limits Renewal Rights
10SP | AEPW | AEPW | DYESS - SOUTH SPRINGDALE 161KV | 53159 SOSPRDL5 161 to 53131 DYESS 5 161 CKT 1 | 313 | 107.9919 | 108.0884 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | Limits Renewal Rights
10SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 111.3118 | 111.4 | LOWELL - TONTITOWN 161KV | 53144 LOWELL 5 161 to 53170 TONTITN5 161 CKT 1 | 0 | Limits Renewal Rights and May be a problem in the 06SP
10SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 109.4136 | 109.4871 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | Limits Renewal Rights and May be a problem in the 06SP
10SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 108.3885 | 108.4758 | LOWELL - ROGERS 161KV | 53144 LOWELL 5 161 to 53152 ROGERS 5 161 CKT 1 | 0 | Limits Renewal Rights and May be a problem in the 06SP
10SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 105.8058 | 105.886 | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | Limits Renewal Rights and May be a problem in the 06SP
10SP | AEPW | AEPW | EAST CENTERTON - GENTRY REC 161KV | 53133 ECNTRTN5 161 to 53187 GENTRYR5 161 CKT 1 | 353 | 105.4272 | 105.4947 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | Limits Renewal Rights and May be a problem in the 06SP
10SP | AEPW | AEPW | EAST FAYETTEVILLE REC - SOUTH SPRINGDALE 161KV | 53193 EFAYTVL5 161 to 53159 SOSPRDL5 161 CKT 1 | 313 | 109.4348 | 109.5348 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | Limits Renewal Rights
10SP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57309 WEMPORI3 115 to 57301 EAST ST3 115 CKT 1 | 92 | 118.035 | 118.1623 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
10SP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57309 WEMPORI3 115 to 57301 EAST ST3 115 CKT 1 | 92 | 103.7738 | 103.8985 | MORRIS COUNTY - WEST EMPORIA 115KV | 57305 MORRIS 3 115 to 57309 WEMPORI3 115 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1209 Outage of the Morris-West Emporia 115kV Line
10SP | AEPW | AEPW | ELM SPRINGS REC - TONTITOWN 161KV | 53194 ELMSPRR5 161 to 53170 TONTITN5 161 CKT 1 | 335 | 109.9897 | 110.1442 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | Limits Renewal Rights
10SP | ENTR | AEPW | EUREKA SPRINGS - OSAGE CREEK (AECC) 161KV | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 107.4938 | 107.7117 | BULL SHOALS - BULL SHOALS HES 161KV | 52660 BULL SH5 161 to 99802 5BULLSH* 161 CKT 1 | 0 | Limits Renewal Rights
10SP | ENTR | AEPW | EUREKA SPRINGS - OSAGE CREEK (AECC) 161KV | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 106.1452 | 106.3641 | BULL SHOALS HES - FLIPPIN 161KV | 99802 5BULLSH* 161 to 99809 5FLIPN 161 CKT 1 | 0 | Limits Renewal Rights
10SP | ENTR | AEPW | EUREKA SPRINGS - OSAGE CREEK (AECC) 161KV | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 103.0871 | 103.3088 | FLIPPIN - SUMMIT 161KV | 99809 5FLIPN 161 to 99837 5SUMMIT 161 CKT 1 | 0 | Limits Renewal Rights
10SP | ENTR | AEPW | EUREKA SPRINGS - OSAGE CREEK (AECC) 161KV | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 100.34 | 100.5585 | BEE BRANCH (AECC) - QUITMAN 161KV | 99519 5QUITMN 161 to 99799 5BEE BR 161 CKT 1 | 0 | Limits Renewal Rights
10SP | AEPW | AEPW | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 313 | 115.8139 | 115.9937 | DYESS - SOUTH SPRINGDALE 161KV | 53131 DYESS 5 161 to 53159 SOSPRDL5 161 CKT 1 | 0 | Limits Renewal Rights
10SP | AEPW | AEPW | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53195 FARMGTN5 161 to 53157 SFAYTVL5 161 CKT 1 | 313 | 104.2903 | 104.7914 | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | Limits Renewal Rights
10SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 114.7029 | 114.7905 | LOWELL - TONTITOWN 161KV | 53144 LOWELL 5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 112.8072 | 112.8824 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 111.783 | 111.8702 | LOWELL - ROGERS 161KV | 53144 LOWELL 5 161 to 53152 ROGERS 5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 109.1909 | 109.271 | CHAMBER SPRINGS - TONTITOWN 161KV | 53154 CHAMSPR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | FLINT CREEK - GENTRY REC 161KV | 53187 GENTRYR5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 108.8059 | 108.8743 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10SP | AEPW | AEPW | FLINT CREEK - TONTITOWN 161KV | 53170 TONTITN5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 117.0245 | 117.1479 | CHAMBER SPRINGS 345/161KV TRANSFORMER | 53154 CHAMSPR5 161 to 53155 CHAMSPR7 345 to 53120 CHAMSPR113.8 CKT 1 | 0 | Limits Renewal Rights
10SP | AEPW | AEPW | FLINT CREEK - TONTITOWN 161KV | 53170 TONTITN5 161 to 53139 FLINTCR5 161 CKT 1 | 353 | 117.023 | 117.1462 | CHAMBER SPRINGS - CLARKSVILLE 345KV | 53155 CHAMSPR7 345 to 53756 CLARKSV7 345 CKT 1 | 0 | Limits Renewal Rights
10SP | WERE | WERE | GRANT JCT - MAHANNA 69KV | 57738 MAHANNA2 69 to 57800 GRANT J2 69 CKT 1 | 101 | 149.8251 | 149.903 | EVANS ENERGY CENTER NORTH - SEDGWICK COUNTY NO. 12 COLWICH 138KV | 57040 EVANS N4 138 to 57065 SG12COL4 138 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1105 Outage of the Moundridge to Halstead 138 kV line, Gordon Evans to Halstead 138 kV line or loss of the Halstead 138 kV bus.
10SP | WERE | WERE | GRANT JCT - RIPLEY 69KV | 57800 GRANT J2 69 to 57832 RIPLEYM2 69 CKT 1 | 108 | 158.3037 | 158.3769 | EVANS ENERGY CENTER NORTH - SEDGWICK COUNTY NO. 12 COLWICH 138KV | 57040 EVANS N4 138 to 57065 SG12COL4 138 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 1105 Outage of the Moundridge to Halstead 138 kV line, Gordon Evans to Halstead 138 kV line or loss of the Halstead 138 kV bus.
10SP | AEPW | AEPW | HUGO - VALLEY TIMBER 69KV | 54018 HUGO---2 69 to 54019 VALYTIM2 69 CKT 1 | 48 | 101.3049 | 101.7476 | ALLEN NATURAL GAS TAP - TUPELO 138KV | 52800 TUPELO 4 138 to 54006 ALLENGT4 138 CKT 1 | 0 | Possible Invalid Contingency
10SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 210.3921 | 210.5237 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 1 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 1 | 68 | 169.7796 | 169.956 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 184.1499 | 184.2651 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | KEENE - SOUTH ALMA 115KV CKT 2 | 57339 S ALMA 3 115 to 57167 KEENE 3 115 CKT 2 | 92 | 148.6245 | 148.7789 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | WERE | WERE | KELLY - SOUTH SENECA 115KV | 57217 KELLY 3 115 to 57337 SENECA 3 115 CKT 1 | 92 | 100.162 | 100.2668 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | GRDA | GRDA | KINZIE 138/69KV TRANSFORMER | 54513 KINZEGR2 69 to 54510 KINZEGR4 138 CKT 1 | 56 | 132.6152 | 132.8201 | CENTRAL - STILLWATER 69KV | 54453 CENTRL 2 69 to 96845 2STILWTR 69 CKT 1 | 0 | Solution Undetermined
10SP | SPS | SPS | LUBBOCK EAST INTERCHANGE 230/115KV TRANSFORMER | 51689 LUBE6 230 to 51688 LUBE3 115 CKT 1 | 172.5 | 113.7052 | 113.7982 | LUBBOCK SOUTH INTERCHANGE 230/115KV TRANSFORMER | 51680 LUBS3 115 to 51681 LUBS6 230 CKT 1 | 0 | May be relieved due to Xcel Energy Transmission Operating Directive for Loss of the 230/115 kV autotransformer at Lubbock South
10SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57335 MCDOWEL3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 191.4692 | 191.6258 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 1 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 1 | 68 | 153.1163 | 153.289 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57335 MCDOWEL3 115 to 57340 SMANHAT3 115 CKT 2 | 92 | 167.2275 | 167.3642 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | MCDOWELL CREEK SWITCHING STATION - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57335 MCDOWEL3 115 CKT 2 | 92 | 133.7145 | 133.8653 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | ENTR | AEPW | MURFREESBORO - SOUTH NASHVILLE 138KV | 99389 4MURFRE 138 to 53321 SNASHVL4 138 CKT 1 | 118 | 102.0119 | 102.0735 | 3BISMRK - HOT SPRINGS WEST BUS 115KV | 99397 3BISMRK 115 to 99403 3HSEHVW 115 CKT 1 | 0 | Limits Renewal Rights
10SP | AEPW | AEPW | PATTERSON - SOUTH NASHVILLE 138KV | 53321 SNASHVL4 138 to 53306 PATTERS4 138 CKT 1 | 118 | 122.4193 | 122.4841 | 3BISMRK - HOT SPRINGS WEST BUS 115KV | 99397 3BISMRK 115 to 99403 3HSEHVW 115 CKT 1 | 0 | Limits Rollover Rights
10SP | AEPW | AEPW | SNYDER - TIPTON & HEADERICK 69KV | 54125 HEADRIK2 69 to 54138 SNYDER-2 69 CKT 1 | 53 | 113.876 | 114.5319 | HOBART JCT - TAMARAC TAP 138KV | 54126 HOB-JCT4 138 to 54158 TAMARTP4 138 CKT 1 | 0 | Limits Renewal Rights and May be a problem in the 06SP
10SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 1 | 68 | 194.5169 | 194.6618 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 1 | 57339 S ALMA 3 115 to 57340 SMANHAT3 115 CKT 1 | 68 | 155.6556 | 155.829 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 169.9649 | 170.0916 | EAST MANHATTAN 230/115KV TRANSFORMER CKT 1 | 56861 EMANHAT6 230 to 57326 EMANHAT3 115 to 56888 EMANHAT118.0 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 633 Outage of the East Manhattan 230-115kV Transformer
10SP | WERE | WERE | SOUTH ALMA - SOUTH MANHATTAN 115KV CKT 2 | 57340 SMANHAT3 115 to 57339 S ALMA 3 115 CKT 2 | 92 | 135.9833 | 136.1346 | EAST MANHATTAN - JEFFREY ENERGY CENTER 230KV CKT 1 | 56852 JEC 6 230 to 56861 EMANHAT6 230 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 900 Outage of the JEC-East Manhattan 230kV Line
10SP | EMDE | EMDE | SUB 383 - MONETT 161/69KV TRANSFORMER | 59480 MON383 5 161 WND 1 MONETT 1 | 150 | 102.4721 | 102.5542 | SUB 124 - AURORA H.T. - SUB 383 - MONETT 161KV CKT 1 | 59468 AUR124 5 161 to 59480 MON383 5 161 CKT 1 | 0 | Limits Renewal Rights
10SP | GRDA | GRDA | COLLINSVILLE 161/69KV TRANSFORMER CKT 1 | 54427 COLINS 5 161 to 54476 COLNSGR2 69 CKT 1 | 50 | 99.8062 | 100.2877 | COLLINSVILLE 161/69KV TRANSFORMER CKT 2 | 54427 COLINS 5 161 to 54476 COLNSGR2 69 CKT 2 | 483.0055 | Limits Renewal Rights
10SP | ENTR | AEPW | EUREKA SPRINGS - OSAGE CREEK (AECC) 161KV | 99832 5OSAGE # 161 to 53136 EUREKA 5 161 CKT 1 | 223 | 99.7778 | 100.0009 | HARRISON-EAST - SUMMIT 161KV | 99811 5HARR-E 161 to 99837 5SUMMIT 161 CKT 1 | 1195.1583 | Limits Renewal Rights
10SP | AEPW | AEPW | BLUE CIRCLE - CATOOSA 69KV | 53806 BCIRCLE2 69 to 53811 CATOOSA2 69 CKT 1 | 72 | 110.1457 | 110.4323 | LYNN LANE TAP - LYNN LANE WEST TAP 138KV | 53782 LLAN WT4 138 to 53816 LLANETP4 138 CKT 1 | 1200 | Invalid Contingency
10SP | AEPW | AEPW | MCALESTER - WELEETKA 69KV | 54024 MCALEST2 69 to 54029 WELEETK2 69 CKT 1 | 52 | 141.5609 | 141.6889 | LONE OAK - SOUTH MCALESTER TAP 138KV | 54022 LONEOAK4 138 to 54032 SMCALTP4 138 CKT 1 | 1200 | Invalid Contingency
10WP | WERE | WERE | 166TH STREET - JARBALO JCT SWITCHING STATION 115KV | 57244 JARBALO3 115 to 57233 166TH 3 115 CKT 1 | 97 | 103.0931 | 103.154 | MIDLAND JCT - PENTAGON 115KV | 57252 MIDLAND3 115 to 57261 PENTAGN3 115 CKT 1 | 0 | Limits Rollover Rights
10WP | WERE | WERE | ANZIO - FORT JCT SWITCHING STATION 115KV | 57321 ANZIO 3 115 to 57328 FT JCT 3 115 CKT 1 | 92 | 101.5493 | 101.6125 | Multiple Outage Contingency: FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | Multiple Outage Contingency: 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 0 | May be relieved due to Westar Transmission Operating Directive 1217 Outage of the Fort JCT-West JCT City 115kV Line
10WP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 275 | 120.0148 | 120.8552 | CHAMBER SPRINGS - FARMINGTON AECC 161KV | 53154 CHAMSPR5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10WP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 275 | 110.7074 | 111.1905 | FLINT CREEK - TONTITOWN 161KV | 53139 FLINTCR5 161 to 53170 TONTITN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10WP | AEPW | AEPW | CHAMBER SPRINGS - TONTITOWN 161KV | 53170 TONTITN5 161 to 53154 CHAMSPR5 161 CKT 1 | 275 | 106.1505 | 106.9979 | FARMINGTON AECC - SOUTH FAYETTEVILLE 161KV | 53157 SFAYTVL5 161 to 53195 FARMGTN5 161 CKT 1 | 0 | See Previous Upgrade Specified
10WP | WERE | WERE | CIRCLEVILLE - HOYT HTI SWITCHING JCT 115KV | 57165 HTI JCT3 115 to 57152 CIRCLVL3 115 CKT 1 | 97 | 114.1283 | 114.3855 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
10WP | WERE | WERE | CIRCLEVILLE - KING HILL N.M. COOP 115KV | 57152 CIRCLVL3 115 to 57331 KING HL3 115 CKT 1 | 92 | 107.7627 | 108.0232 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
10WP | WERE | WERE | EAST STREET - WEST EMPORIA 115KV | 57301 EAST ST3 115 to 57309 WEMPORI3 115 CKT 1 | 92 | 107.2281 | 107.4065 | MORRIS COUNTY 230/115KV TRANSFORMER CKT 1 | 56863 MORRIS 6 230 to 57305 MORRIS 3 115 to 56890 MORRIS 113.8 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 625 Outage of the Morris 230/115kV Transformer
10WP | WERE | WERE | KELLY - KING HILL N.M. COOP 115KV | 57331 KING HL3 115 to 57217 KELLY 3 115 CKT 1 | 92 | 105.5618 | 105.8206 | HOYT - STRANGER CREEK 345KV | 56765 HOYT 7 345 to 56772 STRANGR7 345 CKT 1 | 0 | May be relieved due to Westar Transmission Operating Directive 803 Outage of the Hoyt to Stranger 345 kV line
10WP | SWPA | SWPA | NORFORK 161/69KV TRANSFORMER CKT 2 | 52650 NORFORK269.0 WND 1 NFK X2 1 | 25 | 100.3461 | 100.8602 | NORFORK 161/69KV TRANSFORMER CKT 1 | 52648 NORFORK5 161 to 52650 NORFORK269.0 to 52649 NFK X1 113.8 CKT 1 | 0 | See Previous Upgrade Specified
10WP | WERE | WERE | NORTH AMERICAN PHILIPS - NORTH AMERICAN PHILIPS JCT (SOUTH) 115KV | 57372 PHILIPS3 115 to 57374 SPHILPJ3 115 CKT 1 | 160 | 124.4968 | 124.7493 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
10WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 1 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 1 | 68 | 134.379 | 134.6514 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
10WP | WERE | WERE | NORTH AMERICAN PHILIPS JCT (SOUTH) - WEST MCPHERSON 115KV CKT 2 | 57374 SPHILPJ3 115 to 57438 WMCPHER3 115 CKT 2 | 92 | 117.2635 | 117.5015 | EAST MCPHERSON - SUMMIT 230KV CKT 1 | 56872 EMCPHER6 230 to 56873 SUMMIT 6 230 CKT 1 | 0 | See Previous Upgrade Specified
10WP | WERE | WERE | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 1 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 1 | 68 | 105.3721 | 105.4545 | FORT JCT SWITCHING STATION - WEST JCT CITY JCT (EAST) 115KV CKT 2 | 57328 FT JCT 3 115 to 57343 WJCCTYE3 115 CKT 2 | 1200 | Invalid Contingency
[11 empty] | Total Estimated Cost | 43722400

## Table 3a
Study Case | From Area | To Area | Monitored Branch Over 100% Rate B | Monitored Branch Over 100% Rate B | Rate <MVA> | BC % Loading | TC % Loading | Outaged Branch Causing Overload | Outaged Branch Causing Overload | ATC (MW) | Solution | Cost
04G | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 128.0588 | 134.3078 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 61.3256 | 105.8808 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 849 | Solution Undetermined
04G | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 287 | 51.8102 | 101.7767 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1096 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 23.8949 | 104.9512 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1119 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 23.8473 | 104.7465 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1122 | Solution Undetermined
04G | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 68.8342 | 100.2297 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1165 | Solution Undetermined
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 89.3825 | 108.4922 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 448 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 89.3825 | 108.4922 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 448 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 86.9677 | 104.6083 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 561 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 86.9677 | 104.6083 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 561 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 61.177 | 120.4458 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 641 | Solution Undetermined
04SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 75.8646 | 118.1058 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 693 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.1793 | 115.3291 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 725 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 79.5277 | 108.1188 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 734 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 78.0831 | 105.1867 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 820 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 72.0583 | 107.6152 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 833 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 31.2196 | 112.45 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 854 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 71.2839 | 106.813 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 857 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 53.5333 | 108.8119 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 871 | Solution Undetermined
04SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 72.303 | 105.3333 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 897 | Solution Undetermined
04SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 61.5085 | 105.5967 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 903 | Solution Undetermined
04SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 60.1446 | 104.1889 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 926 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 47.0986 | 106.0603 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 932 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 50.3407 | 107.9591 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 934 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 18.8479 | 111.1576 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 944 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 49.0751 | 105.2298 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1001 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 49.4909 | 104.7177 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 1018 | Solution Undetermined
04SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 74.9286 | 102.3414 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1046 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.375 | 101.4217 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1062 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 20.9385 | 108.8463 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1076 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 20.8952 | 108.6301 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1079 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 19.9992 | 102.5785 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1116 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 48.2291 | 101.9917 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1121 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 8.12 | 100.9991 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1174 | Solution Undetermined
04SP | OKGE | OKGE | ADA OC PUMP TAP - LULA 69KV | 55190 AOCPT 2 69 to 55191 LULA 2 69 CKT 1 | 48 | 116.5913 | 116.6505 | VALLY VIEW - VALLY VIEW TAP 69KV CKT 1 | 55181 VALYVUT2 69 to 55182 VALLYVU2 69 CKT 1 | 1200 | Invalid Contingency
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 24.4963 | 111.3022 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1042 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 24.4456 | 111.074 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1045 | Solution Undetermined
04SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 70.4239 | 101.5032 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1123 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 40.7022 | 101.5963 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1164 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 51.6201 | 100.5065 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1185 | Solution Undetermined
04FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 131.8651 | 138.6012 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID269.0 to 54725 HEMLKTP269.0 CKT 1 | 48 | 101.6661 | 102.4583 | SOUTH 4TH ST 138/69KV TRANSFORMER CKT 1 | 54730 SO4TH2 269.0 to 54731 SO4TH4 4 138 to 55758 SO4TH 1113.2 CKT 1 | 0 | Possible Invalid Contingency
04FA | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 98.4895 | 101.0501 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 755 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 15.8973 | 102.4017 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1167 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 15.8644 | 102.179 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1170 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 61.3903 | 106.9222 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1045 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 17.4973 | 104.2902 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1141 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 17.4595 | 104.0793 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1144 | Solution Undetermined
05G | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 121.5266 | 129.9813 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 25.6171 | 111.5113 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1017 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 25.5644 | 111.2824 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1021 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 38.382 | 104.0455 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1071 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 14.4364 | 102.1997 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1152 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 23.8727 | 100.2539 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1193 | Solution Undetermined
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 95.1656 | 116.882 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 202 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 95.1656 | 116.882 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 202 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 92.5793 | 112.3642 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 313 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 92.5793 | 112.3642 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 313 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 82.828 | 129.8523 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 553 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 81.2205 | 112.1448 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 667 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 58.8161 | 117.5259 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 699 | Solution Undetermined
05SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 60.7934 | 100.584 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 750 | May be able to increase CTR (if relays will coordinate) at Shawnee sub. | 5000
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 79.604 | 108.7057 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 753 | Solution Undetermined
05SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 92.877 | 99.7896 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT1 | 772.6075 | At 800 MW the loading 100.3% and the facility is relieved by additional 200 MW, Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 78.1559 | 114.8452 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 786 | Solution Undetermined
05SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 1 PAOLI 1 1 | 50 | 92.7254 | 99.6396 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT1 | 786.0458 | At 800 MW the loading 100.2% and the facility is relieved by additional 200 MW, Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 53.5109 | 112.0373 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 788 | Solution Undetermined
05SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 69.6758 | 98.8043 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 808.195 | At 1000 MW the loading 102.4% and the facility is relieved by additional 200 MW, Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 76.6436 | 110.0406 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 813 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 66.6153 | 113.0913 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 846 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 30.3718 | 112.9355 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 849 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 64.2971 | 113.6967 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 853 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 51.2378 | 110.0297 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 889 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 72.2812 | 105.2649 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 895 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 52.6718 | 110.5808 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 915 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 70.3097 | 103.0015 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 935 | Solution Undetermined
05SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 68.627 | 104.7184 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 936 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 17.4765 | 111.0196 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 942 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 58.464 | 105.0975 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 943 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 49.9485 | 107.2728 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 948 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 74.3875 | 102.853 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 949 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 69.1638 | 101.7593 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 957 | Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 64.6159 | 102.6783 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 962 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 50.3789 | 106.4434 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 963 | Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 66.2283 | 102.1575 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 963 | Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 56.1242 | 100.5014 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 999 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 49.0933 | 103.6777 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1047 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 43.8857 | 102.1278 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 1068 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 18.2707 | 106.5145 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1109 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 18.2325 | 106.2998 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1112 | Solution Undetermined
05SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 18.5641 | 102.3042 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1118 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.1128 | 100.0275 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1197 | Solution Undetermined
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 95.6503 | 124.478 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 49.7272 | 118.3921 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SH | OKGE | OKGE | PECAN CREEK 345/161KV TRANSFORMER | 55235 PECANCK7 345 WND 2 PECANCK1 1 | 370 | 100.4441 | 102.288 | FT SMITH - MUSKOGEE 345KV CKT 1 | 55224 MUSKOGE7 345 to 55302 FTSMITH7 345 CKT 1 | 0 | Add 2nd 345/161 kV 369MVA transformer. | 3000000
05SH | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 94.677 | 116.1 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 105 | Solution Undetermined
05SH | OKGE | OKGE | PECAN CREEK 345/161KV TRANSFORMER | 55234 PECANCK5 161 WND 1 PECANCK1 1 | 370 | 99.2108 | 100.996 | FT SMITH - MUSKOGEE 345KV CKT 1 | 55224 MUSKOGE7 345 to 55302 FTSMITH7 345 CKT 1 | 296 | See Previous Upgrade Specified
05SH | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 84.612 | 101.3424 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 720 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 76.7064 | 108.4902 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 769 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 72.3026 | 104.0134 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 1005 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 56.3409 | 105.6108 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1045 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 23.1872 | 109.9764 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1060 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 23.1392 | 109.7554 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1063 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 44.4938 | 105.5133 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1081 | Solution Undetermined
05FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 122.2519 | 128.7736 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05FA | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 93.7042 | 104.6854 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 266 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 13.5194 | 100.4148 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1194 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 13.4907 | 100.2042 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1197 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 22.6271 | 109.0302 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1075 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 22.5793 | 108.8081 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1078 | Solution Undetermined
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 96.9575 | 123.0482 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 133 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 96.9575 | 123.0482 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 133 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 94.1343 | 117.8324 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 261 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 94.1343 | 117.8324 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 261 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 95.5738 | 104.2151 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 460 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 95.4116 | 104.0547 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 483 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 81.5991 | 135.5241 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 571 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 83.1507 | 117.2839 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 600 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 94.0801 | 102.6304 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 637 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 93.9284 | 102.485 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 650 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 59.8058 | 124.3562 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 671 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 81.4682 | 113.3307 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 684 | Solution Undetermined
07SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 62.2874 | 111.4199 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 700 | See Previous Upgrade Specified
07SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55074 FRSTHIL2 69 to 55071 TECUMSH2 69 CKT 1 | 72 | 71.8761 | 107.7186 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 729 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 54.2323 | 118.539 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 762 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 77.9456 | 117.2993 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 807 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 78.2366 | 120.3276 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 817 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 29.275 | 117.6526 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 828 | Solution Undetermined
07SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 98.3301 | 102.0828 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 852 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 52.0315 | 114.5199 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 853 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 66.3383 | 120.5308 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 872 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 86.6782 | 104.325 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 879 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 63.7734 | 120.9346 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 882 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 76.1786 | 107.6193 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 889 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 73.2926 | 112.1553 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 893 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 50.7247 | 111.6398 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 906 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 51.1654 | 110.3893 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 914 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.4414 | 106.2683 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 917 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 15.6526 | 114.5077 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 924 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 71.1877 | 109.6554 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 933 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 51.2321 | 117.5561 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 957 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 44.1187 | 108.0189 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 964 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 58.3025 | 112.5134 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 970 | Solution Undetermined
07SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 68.1178 | 109.5127 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 971 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 49.8622 | 107.4988 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 975 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 67.0005 | 108.913 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 979 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 65.2222 | 109.293 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 983 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 74.6599 | 103.8427 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 983 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 69.9653 | 108.3095 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1021 | Solution Undetermined
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 16.1156 | 105.7521 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1052 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 56.1024 | 106.9398 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1065 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 48.0189 | 104.0258 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1070 | Solution Undetermined
07SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 75.4536 | 105.5218 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1074 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 60.7476 | 104.5231 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1090 | Solution Undetermined
07SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 67.2444 | 102.5657 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 1094 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 68.171 | 102.5846 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1104 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 61.2085 | 103.1529 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1121 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - HAYMAKER 138KV | 54898 CIMARON4 138 to 54863 HAYMAKR4 138 CKT 1 | 308 | 73.1158 | 101.4585 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 1125 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 66.5057 | 101.7953 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 1126 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 16.6609 | 105.3371 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1128 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 16.6256 | 105.1213 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1131 | Solution Undetermined
07SP | OKGE | OKGE | HEFNER - TULSA 138KV | 54847 TULSA 4 138 to 54848 HEFNER 4 138 CKT 1 | 222 | 80.7824 | 101.1194 | 84TH ST - TENNESSEE TAP 138KV | 54837 TENESTP4 138 to 54843 84TH ST4 138 CKT 1 | 1144 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 3.1828 | 102.4003 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1149 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 17.8668 | 100.4984 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 1184 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 16.539 | 100.2495 | DRAPER LAKE - POOST ROAD 138KV | 54933 DRAPER 4 138 to 54965 POSTRDT4 138 CKT 1 | 1192 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 17.7807 | 100.2318 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1193 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 19.87 | 107.2834 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1099 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 19.8284 | 107.0652 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1101 | Solution Undetermined
10SP | OKGE | AEPW | BONANZA - BONANZA TAP 161KV | 55261 BONANZT5 161 to 53126 BONANZA5 161 CKT 1 | 177 | 101.898 | 102.2532 | AES - TARBY 161KV | 55262 AES 5 161 to 55264 TARBY 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 100.8972 | 129.5462 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 0 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 100.8972 | 129.5462 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 0 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 101.2712 | 104.9279 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 97.791 | 123.9418 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 96 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 97.791 | 123.9418 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 96 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 97.9722 | 106.8968 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 212 | Solution Undetermined
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 97.7933 | 106.7185 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 230 | Solution Undetermined
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 96.3101 | 105.0008 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 373 | Solution Undetermined
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 96.1428 | 104.8355 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 390 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 85.7349 | 120.3134 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 523 | Solution Undetermined
10SP | OKGE | OKGE | PECAN CREEK 345/161KV TRANSFORMER | 55235 PECANCK7 345 WND 2 PECANCK1 1 | 370 | 98.3568 | 101.2326 | CLARKSVILLE - MUSKOGEE 345KV | 53756 CLARKSV7 345 to 55224 MUSKOGE7 345 CKT 1 | 576 | See Previous Upgrade Specified
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 83.9234 | 116.1437 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 607 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 78.0633 | 133.62 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 684 | Solution Undetermined
10SP | OKGE | OKGE | POOST ROAD - SE15TH 138KV | 54993 SE15TH 4 138 to 54965 POSTRDT4 138 CKT 1 | 191 | 58.1334 | 115.4451 | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 704 | May Limit Renewal Rights
10SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 72.4167 | 109.5069 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 730 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.6145 | 121.3671 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 737 | Solution Undetermined
10SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 59.5553 | 110.3927 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 771 | See Previous Upgrade Specified
10SP | OKGE | OKGE | MAUD - SEMINOLE 138KV CKT 2 | 55055 MAUD 4 138 to 55044 SEMINOL4 138 CKT 2 | 287 | 80.5556 | 104.0941 | MAUD - SEMINOLE 138KV CKT 1 | 55044 SEMINOL4 138 to 55055 MAUD 4 138 CKT 1 | 791 | May Limit Renewal Rights
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 78.5371 | 110.3899 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 825 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 76.8596 | 116.8579 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 832 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 76.6962 | 120.0514 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 837 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 59.7839 | 107.9148 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 839 | May Limit Renewal Rights
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 53.0039 | 116.236 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 841 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 28.0806 | 117.5773 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 863 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 49.9546 | 114.412 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 863 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 51.6692 | 113.317 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 892 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 52.0955 | 111.9302 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 900 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 76.8968 | 106.3977 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 923 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 81.8173 | 104.4898 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 924 | May Limit Renewal Rights
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 62.888 | 118.6279 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 925 | Solution Undetermined
10SP | OKGE | OKGE | PECAN CREEK 345/161KV TRANSFORMER | 55235 PECANCK7 345 WND 2 PECANCK1 1 | 370 | 96.8616 | 100.581 | FT SMITH - MUSKOGEE 345KV CKT 1 | 55224 MUSKOGE7 345 to 55302 FTSMITH7 345 CKT 1 | 937 | See Previous Upgrade Specified
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 71.9638 | 111.4564 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 938 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 59.8927 | 118.6218 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 941 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 86.1912 | 103.4081 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 951 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 50.7642 | 108.9976 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 958 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 12.5502 | 112.6273 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 969 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 69.739 | 108.8562 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 989 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 55.284 | 104.0863 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1000 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 63.4423 | 108.6852 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1038 | Solution Undetermined
10SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 65.9224 | 108.5708 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1038 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 46.1293 | 114.4571 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1038 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 65.528 | 108.6073 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1046 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 54.1657 | 109.8027 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1059 | Solution Undetermined
10SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 12.9396 | 103.8247 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1111 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 53.4729 | 105.7632 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1119 | Solution Undetermined
10SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 66.6765 | 102.3259 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 1122 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 308 | 73.0991 | 101.9628 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 1135 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 68.4529 | 107.443 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1144 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 67.0027 | 102.0297 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1144 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 58.1783 | 102.8277 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1147 | Solution Undetermined
10SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 65.8945 | 101.5098 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 1149 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 37.8424 | 101.8379 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 1149 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 59.2572 | 102.2644 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1159 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 44.704 | 101.0578 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1171 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1195 | 12.4723 | 101.1943 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1184 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1195 | 12.4442 | 100.983 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1187 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 16.3051 | 100.1248 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 1196 | Solution Undetermined
10SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 82.1442 | 100.0052 | INGLEWOOD - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55060 INGLEWD4 138 CKT 1 | 1199 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 84.9662 | 170.6205 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 124.5944 | 164.0878 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 67.2348 | 101.2862 | DRAPER LAKE - GM 138KV | 54933 DRAPER 4 138 to 54961 GM 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 69.0425 | 100.5515 | DRAPER LAKE - MIDWEST TAP 138KV | 54933 DRAPER 4 138 to 54946 MIDWEST4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10WP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 72.0542 | 104.7666 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 585 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 19.6757 | 104.8686 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1132 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 19.635 | 104.6486 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1135 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 31.1209 | 102.6538 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1138 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 41.3943 | 101.1704 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1165 | Solution Undetermined
[11 empty] | Total Cost | 3005000

## Table 4a
Study Case | From Area | To Area | Monitored Branch Over 100% Rate B | Monitored Branch Over 100% Rate B | Rate <MVA> | BC % Loading | TC % Loading | Outaged Branch Causing Overload | Outaged Branch Causing Overload | ATC (MW) | Solution | Cost
04G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 61.5437 | 106.1055 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 880 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 32.4515 | 113.796 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 968 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 32.3866 | 113.583 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 971 | Solution Undetermined
04G | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 287 | 50.3913 | 100.9386 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1148 | Solution Undetermined
04SP | OKGE | OKGE | FT SMITH 500/161KV TRANSFORMER | 55305 FTSMITH8 500 WND 2 FTSMITH3 1 | 480 | 101.8088 | 102.4499 | FT SMITH 345/161KV TRANSFORMER CKT 1 | 55300 FTSMITH5 161 to 55302 FTSMITH7 345 to 55728 FTSMIT3113.8 CKT 1 | 0 | OKGE Plans to Install 2nd 500-161kV transformer bank by 12/1/2004
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 88.2839 | 107.7661 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 489 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 88.2839 | 107.7661 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 489 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 85.9134 | 103.809 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 602 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 85.9134 | 103.809 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 602 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 59.6685 | 119.6317 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 658 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 54.669 | 114.478 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 742 | Solution Undetermined
04SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 69.8261 | 112.3307 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 806 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 30.0885 | 112.2662 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 862 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 21.0227 | 114.0066 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 890 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 69.0944 | 105.2105 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 907 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 74.6903 | 103.5414 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 909 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 51.221 | 107.1008 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 913 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 68.3151 | 104.4045 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 930 | Solution Undetermined
04SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 78.2681 | 106.1068 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 942 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 45.5986 | 105.1447 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 959 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 28.7 | 117.0157 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 964 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 48.2782 | 106.7604 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 966 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 28.6409 | 116.7884 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 967 | Solution Undetermined
04SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 67.7829 | 101.1464 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 983 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 22.7806 | 105.8256 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1011 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 14.3713 | 107.3344 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1018 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 47.0652 | 104.0273 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1047 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 47.5073 | 103.2449 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 1075 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 73.4814 | 100.8066 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 1078 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 287 | 48.6877 | 101.8094 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1148 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 51.5304 | 100.6302 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1165 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 46.2981 | 100.5389 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1179 | Solution Undetermined
04SP | OKGE | OKGE | ADA OC PUMP TAP - LULA 69KV | 55190 AOCPT 2 69 to 55191 LULA 2 69 CKT 1 | 48 | 116.3908 | 116.5262 | VALLY VIEW - VALLY VIEW TAP 69KV CKT 1 | 55181 VALYVUT2 69 to 55182 VALLYVU2 69 CKT 1 | 1200 | Invalid Contingency
04SH | OKGE | OKGE | CLEVELAND TAP - SOUTH 4TH ST 69KV | 54730 SO4TH2 2 69 to 54722 CLEVETP2 69 CKT 1 | 92 | 102.8481 | 106.2687 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 32.1722 | 119.1601 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 934 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 32.1057 | 118.9261 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 937 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 43.1373 | 104.3554 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1100 | Solution Undetermined
04SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 68.7767 | 100.2916 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1184 | Solution Undetermined
04SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 40.651 | 100.3743 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1191 | Solution Undetermined
04FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 164.5359 | 171.3184 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID269.0 to 54725 HEMLKTP269.0 CKT 1 | 48 | 109.2454 | 110.0101 | SOUTH 4TH ST 138/69KV TRANSFORMER CKT 1 | 54730 SO4TH2 269.0 to 54731 SO4TH4 4 138 to 55758 SO4TH 1113.2 CKT 1 | 0 | Possible Invalid Contingency
04FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID2 69 to 54725 HEMLKTP2 69 CKT 1 | 48 | 100.436 | 102.0382 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 23.4884 | 109.9903 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1062 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 23.4398 | 109.7643 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1065 | Solution Undetermined
04FA | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 69.7295 | 101.7149 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1132 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 49.8559 | 100.24 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1194 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 63.7476 | 110.0539 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 965 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 25.3252 | 112.9266 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1024 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 25.2729 | 112.7062 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1027 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 60.7908 | 103.4886 | KETCH - OMPA-FAIRVIEW 138KV | 54834 KETCH 4 138 to 56173 OMFAIRF4 138 CKT 1 | 1123 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 36.5812 | 102.8784 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1147 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 53.0289 | 101.9957 | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 1157 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 52.456 | 101.7069 | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 1164 | Solution Undetermined
05AP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 30.9226 | 107.6095 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1093 | Solution Undetermined
05AP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 30.8586 | 107.3962 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1096 | Solution Undetermined
05G | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 169.0068 | 178.1158 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 33.4063 | 120.1483 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 905 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 33.3372 | 119.9216 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 907 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 41.6091 | 107.4758 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 982 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 15.1628 | 106.0769 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1073 | Solution Undetermined
05G | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 13.6622 | 104.8472 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1092 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 44.0408 | 101.1985 | KETCH - OMPA-FAIRVIEW 138KV | 54834 KETCH 4 138 to 56173 OMFAIRF4 138 CKT 1 | 1164 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 22.089 | 100.6809 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1182 | Solution Undetermined
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 94.4754 | 116.4696 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 232 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 94.4754 | 116.4696 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 232 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 91.9321 | 111.8861 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 342 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 91.9321 | 111.8861 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 342 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 75.9484 | 123.3339 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 694 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.5048 | 116.7843 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 713 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 77.0861 | 108.2266 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 796 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 52.1982 | 111.2862 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 804 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 29.6824 | 112.905 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 852 | Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 73.039 | 110.0926 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 862 | Solution Undetermined
05SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 68.5135 | 98.1043 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 871.3856 | At 1000 MW the loading 101.7% and the facility is relieved by additional 200 MW, Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 75.7172 | 105.0142 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 879 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 20.2449 | 114.1561 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 887 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 49.4274 | 109.0143 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 913 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 69.8319 | 103.7016 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 927 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 56.7223 | 106.5995 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 930 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 58.1067 | 105.1095 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 937 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 46.5018 | 104.8497 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 964 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 48.1835 | 106.265 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 971 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 26.5458 | 115.2247 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 989 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 26.4909 | 114.998 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 991 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 48.6467 | 105.1755 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 993 | Solution Undetermined
05SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 21.6119 | 105.9117 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 995 | Solution Undetermined
05SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 12.6212 | 106.7518 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1021 | Solution Undetermined
05SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 75.8291 | 102.7548 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1022 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 47.4064 | 102.418 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1099 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 42.5832 | 101.3424 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 1117 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 40.2523 | 100.7154 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1178 | Solution Undetermined
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 93.5907 | 122.8359 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 42.0721 | 111.573 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SH | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 88.1225 | 109.8063 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 243 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 75.4671 | 107.7165 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 823 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 31.409 | 118.5771 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 942 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 31.344 | 118.3508 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 944 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 47.3634 | 109.1564 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1011 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 55.8267 | 105.6751 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1045 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 71.0608 | 103.2044 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 1047 | Solution Undetermined
05SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 44.7242 | 104.8238 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1096 | Solution Undetermined
05SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 52.8015 | 101.8163 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1149 | Solution Undetermined
05FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 166.1148 | 172.6099 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID269.0 to 54725 HEMLKTP269.0 CKT 1 | 48 | 107.9604 | 108.9074 | SOUTH 4TH ST 138/69KV TRANSFORMER CKT 1 | 54730 SO4TH2 269.0 to 54731 SO4TH4 4 138 to 55758 SO4TH 1113.2 CKT 1 | 0 | Possible Invalid Contingency
05FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID2 69 to 54725 HEMLKTP2 69 CKT 1 | 48 | 99.2006 | 100.9681 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 510 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 21.8322 | 108.8726 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1077 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 21.7871 | 108.6478 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1080 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 28.2728 | 100.1343 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1196 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 30.5454 | 117.4094 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 960 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 30.4819 | 117.1807 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 963 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 51.427 | 103.1354 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1130 | Solution Undetermined
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 95.9615 | 122.2165 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 179 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 95.9615 | 122.2165 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 179 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 93.1955 | 116.9579 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 303 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 93.1955 | 116.9579 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 303 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 93.8705 | 102.7949 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 656 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 93.7072 | 102.6321 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 671 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 58.8558 | 123.8627 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 681 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 79.202 | 113.4865 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 728 | Solution Undetermined
07SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 60.4663 | 109.8766 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 734 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 75.0257 | 129.2604 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 737 | Solution Undetermined
07SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55074 FRSTHIL2 69 to 55071 TECUMSH2 69 CKT 1 | 72 | 70.5893 | 106.7766 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 759 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 53.2635 | 118.0205 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 773 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 92.3243 | 101.007 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 796 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 98.4736 | 102.4687 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 803 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 77.7699 | 109.7738 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 810 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 92.1715 | 100.8562 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 821 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 28.8419 | 117.6625 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 834 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 18.5162 | 117.6374 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 878 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 50.1491 | 113.3584 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 879 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 40.4017 | 103.5828 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 879 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 73.3585 | 115.7691 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 881 | Solution Undetermined
07SP | OKGE | OKGE | EARLSBORO - FOREST HILL 69KV | 55073 ERLSBOR2 69 to 55074 FRSTHIL2 69 CKT 1 | 48 | 47.1237 | 104.0189 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 906 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 71.3084 | 111.1361 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 915 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 48.8903 | 110.5086 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 930 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 49.3579 | 108.9542 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 946 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 56.462 | 114.018 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 954 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 58.0682 | 112.7002 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 958 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 84.9922 | 102.9301 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 969 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 19.513 | 109.5998 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 969 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 43.1224 | 107.4509 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 974 | Solution Undetermined
07SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 79.2761 | 109.6917 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 979 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 72.5694 | 104.1291 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 993 | Solution Undetermined
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 9.71 | 109.2279 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1003 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 66.6282 | 105.8964 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 1005 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 45.3695 | 112.0363 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1006 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 25.0201 | 114.1933 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1009 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 48.1027 | 106.0925 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1009 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 24.9684 | 113.9652 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1012 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 53.8231 | 103.0551 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1033 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 52.2301 | 106.8463 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1057 | Solution Undetermined
07SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 63.2031 | 104.8934 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1069 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 64.4936 | 103.3916 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 1085 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 59.8577 | 104.267 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1093 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 60.9542 | 103.2288 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1113 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 46.0915 | 102.4261 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1120 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54853 DVISION4 138 CKT 1 | 287 | 63.263 | 102.0132 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1131 | Solution Undetermined
07SP | OKGE | OMPA | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 287 | 48.5668 | 101.8728 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1140 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 51.7743 | 102.9243 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1142 | Solution Undetermined
07SP | OKGE | OKGE | HEFNER - TULSA 138KV | 54847 TULSA 4 138 to 54848 HEFNER 4 138 CKT 1 | 222 | 80.2336 | 100.8829 | 84TH ST - TENNESSEE TAP 138KV | 54837 TENESTP4 138 to 54843 84TH ST4 138 CKT 1 | 1155 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 71.2908 | 100.5835 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1165 | Solution Undetermined
07SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 64.607 | 100.2499 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 1190 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 39.9895 | 100.2484 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1193 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 60.2251 | 104.1571 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1196 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 27.8666 | 115.6276 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 963 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 27.9245 | 115.8535 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 980 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 14.8704 | 103.109 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1126 | Solution Undetermined
10SP | OKGE | OKGE | 3RDST - MULDROW 69KV | 55256 MULDROW2 69 to 55307 3RDST 2 69 CKT 1 | 48 | 102.2882 | 102.7128 | KILGORE - VBI 69KV | 55335 KILGORE2 69 to 55336 VBI 2 69 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | SWPA | BROWN - BROWN 138KV | 55157 BROWN 4 138 to 52802 S BROWN4 138 CKT 1 | 120 | 100.0467 | 101.6967 | GLASSES - RUSSETT 138KV | 55120 RUSSET-4 138 to 55147 GLASSES4 138 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | COLONY - FT SMITH 161KV | 55345 COLONY 5 161 to 55300 FTSMITH5 161 CKT 1 | 335 | 102.1739 | 102.509 | FT SMITH - QUANEX TAP 161KV | 55300 FTSMITH5 161 to 55310 QUANXTP5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | MASSARD 161/69KV TRANSFORMER | 55343 MASSARD5 161 WND 2 MASSARD4 1 | 120 | 103.7371 | 104.0074 | ARKOMA - FTSMITH 161KV CKT 1 | 55300 FTSMITH5 161 to 55306 ARKOMA 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | MASSARD 161/69KV TRANSFORMER | 55342 MASSARD269.0 WND 1 MASSARD4 1 | 120 | 101.1674 | 101.4297 | ARKOMA - FTSMITH 161KV CKT 1 | 55300 FTSMITH5 161 to 55306 ARKOMA 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | MASSARD 161/69KV TRANSFORMER | 55343 MASSARD5 161 WND 2 MASSARD4 1 | 120 | 100.1216 | 100.393 | 3RDST - ARKOMA 161KV CKT 1 | 55306 ARKOMA 5 161 to 55308 3RDST 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 101.3079 | 105.0732 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 99.5302 | 128.3498 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 20 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 99.5302 | 128.3498 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 20 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 96.4917 | 122.7959 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 153 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 96.4917 | 122.7959 | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 153 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 96.1583 | 105.2395 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 403 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 95.978 | 105.0597 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 422 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 94.435 | 103.2508 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 582 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 94.2665 | 103.0841 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 601 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 82.0175 | 116.8016 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 646 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 80.2657 | 112.7103 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 735 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 55.5703 | 120.5268 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 754 | Solution Undetermined
10SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 70.6619 | 108.1163 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 777 | Solution Undetermined
10SP | OKGE | OKGE | POOST ROAD - SE15TH 138KV | 54993 SE15TH 4 138 to 54965 POSTRDT4 138 CKT 1 | 191 | 52.4634 | 110.556 | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 813 | May Limit Renewal Rights
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 70.8513 | 126.7631 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 823 | Solution Undetermined
10SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 57.0592 | 108.2949 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 826 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 51.3943 | 114.8822 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 868 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 27.3033 | 117.1419 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 872 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 48.8998 | 113.5673 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 880 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 50.1022 | 111.9917 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 919 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 15.3186 | 115.658 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 926 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 71.3859 | 114.9964 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 929 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 50.51 | 110.4737 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 932 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 75.1185 | 107.1682 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 932 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 55.2346 | 103.9961 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 940 | May Limit Renewal Rights
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 287 | 39.8262 | 108.5196 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 964 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 80.4104 | 103.319 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 970 | May Limit Renewal Rights
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 69.8248 | 110.2263 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 973 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 49.2213 | 107.5708 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 989 | Solution Undetermined
10SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 16.185 | 107.3294 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1029 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 52.0671 | 111.2095 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1043 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 54.0566 | 110.2543 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1047 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 73.5358 | 103.2539 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1049 | Solution Undetermined
10SP | OKGE | OKGE | EARLSBORO - FOREST HILL 69KV | 55073 ERLSBOR2 69 to 55074 FRSTHIL2 69 CKT 1 | 48 | 43.0434 | 101.7676 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 1055 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 21.4115 | 110.3862 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1061 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 21.3674 | 110.164 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1064 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 84.4569 | 101.7717 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1069 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 64.9069 | 104.7712 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 1090 | Solution Undetermined
10SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 4.6249 | 105.5031 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1091 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 39.8735 | 103.4775 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1124 | Solution Undetermined
10SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 60.5662 | 103.4857 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1135 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 57.7623 | 103.2456 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1143 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 47.6424 | 103.699 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1147 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 62.6482 | 102.1537 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 1150 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 59.1073 | 102.4619 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1154 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 57.4893 | 102.2388 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1158 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 51.6736 | 100.6286 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1170 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 36.7955 | 100.9766 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 1173 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 48.9303 | 101.4039 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1180 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 61.3544 | 100.7314 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1183 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 39.4549 | 100.2474 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1194 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 43.9596 | 100.1333 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1198 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 75.7863 | 162.5734 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 121.735 | 161.6166 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 27.8062 | 113.0445 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1019 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 27.7488 | 112.8165 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1022 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 33.4815 | 105.6173 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1070 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 40.452 | 100.9484 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1172 | Solution Undetermined
[11 empty] | Total Cost | 0

## Table 5a
Study Case | From Area | To Area | Monitored Branch Over 100% Rate B | Monitored Branch Over 100% Rate B | Rate <MVA> | BC % Loading | TC % Loading | Outaged Branch Causing Overload | Outaged Branch Causing Overload | ATC (MW) | Solution | Cost
04G | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 155.299 | 162.4094 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04G | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 287 | 64.0015 | 114.7295 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 742 | Solution Undetermined
04G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 66.5345 | 111.4137 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 748 | Solution Undetermined
04G | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 71.5605 | 103.3419 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 914 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 35.7162 | 116.906 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 917 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 35.6448 | 116.6827 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 920 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - HORSESHOE LAKE 138KV | 54907 ARCADIA4 138 to 54941 HSL 4 138 CKT 1 | 287 | 42.3592 | 102.2025 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1139 | Solution Undetermined
04G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 57.929 | 100.9152 | KETCH - OMPA-FAIRVIEW 138KV | 54834 KETCH 4 138 to 56173 OMFAIRF4 138 CKT 1 | 1146 | Solution Undetermined
04G | OKGE | OKGE | ARCADIA - HORSESHOE LAKE 138KV | 54907 ARCADIA4 138 to 54941 HSL 4 138 CKT 1 | 287 | 52.9586 | 100.5813 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1175 | Solution Undetermined
04G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 52.9549 | 100.414 | ARCADIA - HORSESHOE LAKE 138KV | 54907 ARCADIA4 138 to 54941 HSL 4 138 CKT 1 | 1180 | Solution Undetermined
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 87.6328 | 107.0291 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 513 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 87.6328 | 107.0291 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 513 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 64.4607 | 124.116 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 582 | Solution Undetermined
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 85.278 | 103.1572 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 628 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 85.278 | 103.1572 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 628 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 59.4684 | 118.9846 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 666 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 80.1048 | 108.8351 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 711 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 74.3187 | 110.2437 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 763 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.4122 | 113.0396 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 779 | Solution Undetermined
04SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 73.5407 | 109.439 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 784 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 34.1891 | 116.0008 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 785 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 78.7003 | 105.8647 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 791 | Solution Undetermined
04SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 70.051 | 112.5661 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 802 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 50.4084 | 109.7027 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 832 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 23.7069 | 116.4774 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 842 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 287 | 61.9354 | 114.9635 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 879 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 51.5762 | 109.7243 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 889 | Solution Undetermined
04SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 81.153 | 108.7723 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 889 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 32.0798 | 120.1404 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 922 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 32.0134 | 119.9123 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 925 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 25.8726 | 108.7624 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 938 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 58.1457 | 107.0491 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 939 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 50.2798 | 106.9555 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 956 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 50.7402 | 106.2258 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 971 | Solution Undetermined
04SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 67.98 | 101.2835 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 980 | Solution Undetermined
04SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 16.079 | 108.9619 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 981 | Solution Undetermined
04SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.6372 | 101.9911 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1009 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 65.3397 | 102.46 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1053 | Solution Undetermined
04SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 58.5773 | 102.2005 | QUAIL CREEK - SKYLINE 138KV | 54850 SKYLINE4 138 to 54851 QUAILCK4 138 CKT 1 | 1058 | Solution Undetermined
04SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 49.4474 | 103.4476 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 1064 | Solution Undetermined
04SP | OKGE | OMPA | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 287 | 52.4492 | 101.5375 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1114 | Solution Undetermined
04SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 73.7442 | 100.3054 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1151 | Solution Undetermined
04SP | OKGE | OKGE | ADA OC PUMP TAP - LULA 69KV | 55190 AOCPT 2 69 to 55191 LULA 2 69 CKT 1 | 48 | 116.6409 | 116.7344 | VALLY VIEW - VALLY VIEW TAP 69KV CKT 1 | 55181 VALYVUT2 69 to 55182 VALLYVU2 69 CKT 1 | 1200 | Invalid Contingency
04SH | OKGE | OKGE | CLEVELAND TAP - SOUTH 4TH ST 69KV | 54730 SO4TH2 2 69 to 54722 CLEVETP2 69 CKT 1 | 92 | 104.2127 | 107.6798 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 35.516 | 122.3168 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 890 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 35.4424 | 122.0709 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 893 | Solution Undetermined
04SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 73.3612 | 104.7472 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 947 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 45.6705 | 106.9311 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1041 | Solution Undetermined
04SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 54.7205 | 103.9754 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1081 | Solution Undetermined
04SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 42.2893 | 102.1074 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1150 | Solution Undetermined
04SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 69.227 | 100.569 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 1169 | Solution Undetermined
04FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 166.2433 | 173.1911 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID269.0 to 54725 HEMLKTP269.0 CKT 1 | 48 | 108.8949 | 109.7339 | SOUTH 4TH ST 138/69KV TRANSFORMER CKT 1 | 54730 SO4TH2 269.0 to 54731 SO4TH4 4 138 to 55758 SO4TH 1113.2 CKT 1 | 0 | Possible Invalid Contingency
04FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID2 69 to 54725 HEMLKTP2 69 CKT 1 | 48 | 100.2395 | 101.9056 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
04FA | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 73.7162 | 105.6324 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 977 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 26.9565 | 113.4462 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1013 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 26.9005 | 113.2045 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1016 | Solution Undetermined
04FA | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 52.2567 | 102.7734 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1128 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 67.8344 | 113.556 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 837 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 29.4366 | 116.5469 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 974 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 29.3757 | 116.3171 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 977 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 63.3572 | 105.4914 | KETCH - OMPA-FAIRVIEW 138KV | 54834 KETCH 4 138 to 56173 OMFAIRF4 138 CKT 1 | 1076 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 56.3979 | 104.7154 | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 1097 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 39.4415 | 105.2913 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1102 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 55.6009 | 104.2147 | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 1108 | Solution Undetermined
04WP | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54835 MEMRIAL4 138 to 54832 EASTERN4 138 CKT 1 | 191 | 59.733 | 101.8291 | OMPA-FAIRVIEW - SKYLINE 138KV | 54850 SKYLINE4 138 to 56173 OMFAIRF4 138 CKT 1 | 1159 | Solution Undetermined
04WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 47.8072 | 101.6569 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1161 | Solution Undetermined
04WP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 36.1527 | 100.75 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1186 | Solution Undetermined
05AP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 35.0746 | 111.5065 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1039 | Solution Undetermined
05AP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 35.0017 | 111.2768 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1042 | Solution Undetermined
05G | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 170.142 | 179.2779 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 37.4342 | 123.8882 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 853 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 37.357 | 123.644 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 856 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 45.1494 | 111.2079 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 887 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 18.4085 | 108.4143 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1027 | Solution Undetermined
05G | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 15.9879 | 106.379 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1059 | Solution Undetermined
05G | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 26.5613 | 104.1817 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1088 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 46.3761 | 103.4932 | KETCH - OMPA-FAIRVIEW 138KV | 54834 KETCH 4 138 to 56173 OMFAIRF4 138 CKT 1 | 1099 | Solution Undetermined
05G | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 23.8749 | 102.6607 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1124 | Solution Undetermined
05G | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 48.5455 | 101.6308 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1129 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 33.1681 | 101.7292 | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 1153 | Solution Undetermined
05G | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 33.6928 | 101.3259 | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 1164 | Solution Undetermined
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 93.8122 | 115.7609 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 258 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 93.8122 | 115.7609 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 258 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 91.2829 | 111.2683 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 368 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 91.2829 | 111.2683 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 368 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 82.7102 | 113.7085 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 615 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 61.8131 | 120.7868 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 645 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 76.258 | 123.593 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 688 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 81.1232 | 110.2282 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 697 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.5137 | 115.3052 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 734 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 33.7257 | 116.6177 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 784 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 23.0205 | 116.716 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 841 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 52.9152 | 112.157 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 842 | Solution Undetermined
05SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 73.296 | 110.2449 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 860 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 51.5838 | 109.3272 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 900 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 75.7607 | 104.2947 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 902 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 52.0636 | 108.3152 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 916 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 56.5205 | 106.3376 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 932 | Solution Undetermined
05SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 24.6964 | 108.7893 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 933 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 69.1469 | 102.9101 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 941 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 30.1773 | 118.5528 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 945 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 46.9087 | 105.3921 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 946 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 30.1147 | 118.321 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 947 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 56.9649 | 103.9444 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 950 | Solution Undetermined
05SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 47.3905 | 105.6361 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 958 | Solution Undetermined
05SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 78.4737 | 105.1806 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 966 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 50.7357 | 105.478 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 983 | Solution Undetermined
05SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 14.4322 | 108.4693 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 983 | Solution Undetermined
05SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 63.0271 | 102.4342 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 993 | Solution Undetermined
05SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 74.3349 | 100.9919 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1042 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 50.1559 | 101.208 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1106 | Solution Undetermined
05SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 41.5 | 101.7792 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1145 | Solution Undetermined
05SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 63.7311 | 100.0799 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1149 | Solution Undetermined
05SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.0535 | 100.1935 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 1178 | Solution Undetermined
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 90.402 | 119.5817 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54988 TINKER44 138 to 54990 TINKER24 138 CKT 1 | 100 | 37.9744 | 107.2978 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
05SH | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 88.1821 | 109.8885 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 239 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 79.6542 | 111.7196 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 589 | Solution Undetermined
05SH | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54850 SKYLINE4 138 to 54835 MEMRIAL4 138 CKT 1 | 287 | 75.2602 | 107.2348 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 844 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 35.1239 | 121.9818 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 894 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 35.0511 | 121.7428 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 896 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 59.8305 | 109.2952 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 942 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 50.0911 | 111.5627 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 954 | Solution Undetermined
05SH | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 84.2886 | 101.4881 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 1042 | Solution Undetermined
05SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 46.5287 | 106.4101 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1060 | Solution Undetermined
05SH | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 55.8257 | 104.6027 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1069 | Solution Undetermined
05SH | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 60.8512 | 101.8345 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 1139 | Solution Undetermined
05FA | OKGE | OKGE | CLEVELAND TAP - IMO 69KV | 54722 CLEVETP2 69 to 54721 IMO 2 69 CKT 1 | 36 | 169.0882 | 175.8672 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 0 | Solution Undetermined
05FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID269.0 to 54725 HEMLKTP269.0 CKT 1 | 48 | 107.6685 | 108.6947 | SOUTH 4TH ST 138/69KV TRANSFORMER CKT 1 | 54730 SO4TH2 269.0 to 54731 SO4TH4 4 138 to 55758 SO4TH 1113.2 CKT 1 | 0 | Possible Invalid Contingency
05FA | OKGE | OKGE | HEMLOCK TAP - NE ENID 69KV | 54732 NE ENID2 69 to 54725 HEMLKTP2 69 CKT 1 | 48 | 99.0341 | 100.897 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 574 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 25.4421 | 112.4086 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1028 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 25.3894 | 112.1879 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1031 | Solution Undetermined
05FA | OKGE | OKGE | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 191 | 55.4443 | 104.012 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1040 | Solution Undetermined
05FA | OKGE | OKGE | CLEVELAND TAP - SOUTH 4TH ST 69KV | 54730 SO4TH2 2 69 to 54722 CLEVETP2 69 CKT 1 | 92 | 97.6223 | 100.3356 | IMO TAP - SOUTH 4TH ST 138KV | 54731 SO4TH4 4 138 to 54790 IMO TAP4 138 CKT 1 | 1048 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 31.2719 | 103.2837 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1117 | Solution Undetermined
05FA | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 39.9855 | 100.2953 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1190 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 34.547 | 121.1283 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 908 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 34.4756 | 120.8869 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 911 | Solution Undetermined
05WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 54.2737 | 105.4423 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1075 | Solution Undetermined
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 96.7795 | 123.0345 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 142 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 96.7795 | 123.0345 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 142 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 93.9904 | 117.8231 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 268 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 93.9904 | 117.8231 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 268 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 84.4824 | 118.6798 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 554 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 62.4124 | 127.2084 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 627 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 82.8326 | 114.693 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 631 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 93.7605 | 102.581 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 681 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 93.5968 | 102.4182 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 697 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 56.8305 | 121.3809 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 721 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 74.8521 | 129.1463 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 732 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 32.5603 | 121.1479 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 787 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 53.8582 | 116.7618 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 812 | Solution Undetermined
07SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 55.9289 | 105.6682 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 833 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 98.3817 | 102.2302 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 835 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 21.147 | 120.1337 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 845 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 77.4094 | 108.9027 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 848 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 92.1852 | 100.7987 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 852 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 52.5057 | 113.8259 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 864 | Solution Undetermined
07SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 67.4629 | 103.7664 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 868 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 52.993 | 112.3595 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 872 | Solution Undetermined
07SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 92.0323 | 100.648 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 877 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 73.2539 | 115.6424 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 881 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 46.7084 | 110.8428 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 909 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 86.0976 | 103.8786 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 913 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 57.1029 | 106.1601 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 928 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 51.644 | 109.4133 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 931 | Solution Undetermined
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 21.9066 | 111.9447 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 931 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 70.3745 | 110.1382 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 933 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 75.9213 | 105.0934 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 939 | Solution Undetermined
07SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 81.2991 | 111.4569 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 946 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 55.8558 | 113.4598 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 962 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 27.8508 | 116.6974 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 976 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 56.5767 | 111.3079 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 976 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 27.7931 | 116.4625 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 978 | Solution Undetermined
07SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 10.9756 | 110.5581 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 982 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 50.3436 | 106.542 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 993 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 45.7613 | 112.421 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1006 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 63.4839 | 107.303 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1021 | Solution Undetermined
07SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 68.3659 | 103.8816 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 1041 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 65.697 | 104.9542 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 1042 | Solution Undetermined
07SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 67.6251 | 103.1008 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 1072 | Solution Undetermined
07SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 51.6369 | 106.2877 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1074 | Solution Undetermined
07SP | OKGE | OMPA | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 287 | 50.7761 | 103.9175 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1075 | Solution Undetermined
07SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 63.0951 | 104.789 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1076 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 41.9532 | 104.9512 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1081 | Solution Undetermined
07SP | OKGE | OKGE | HEFNER - TULSA 138KV | 54847 TULSA 4 138 to 54848 HEFNER 4 138 CKT 1 | 222 | 81.5953 | 102.0561 | 84TH ST - TENNESSEE TAP 138KV | 54837 TENESTP4 138 to 54843 84TH ST4 138 CKT 1 | 1097 | May Limit Renewal Rights and May be a problem in the 06SP
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 59.4454 | 103.8136 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1108 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 20.1847 | 102.8558 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1118 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 63.5579 | 102.4576 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 1120 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 19.2041 | 101.9555 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 1137 | Solution Undetermined
07SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 52.3543 | 101.1331 | HEFNER - LAKESIDE 138KV | 54848 HEFNER 4 138 to 54849 LAKESID4 138 CKT 1 | 1138 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 52.1173 | 103.1748 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1139 | Solution Undetermined
07SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 59.8798 | 102.152 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1144 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 17.7806 | 101.642 | DRAPER LAKE - POOST ROAD 138KV | 54933 DRAPER 4 138 to 54965 POSTRDT4 138 CKT 1 | 1147 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 41.5463 | 101.7225 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1155 | Solution Undetermined
07SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 18.9088 | 101.5174 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 1156 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 62.3276 | 101.1008 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1164 | Solution Undetermined
07SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 67.1301 | 100.5793 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1177 | Solution Undetermined
07SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 52.273 | 100.8176 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1180 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 31.9118 | 119.4967 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 930 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 31.8458 | 119.2589 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 933 | Solution Undetermined
07WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 18.0807 | 105.6462 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1066 | Solution Undetermined
10SP | OKGE | AEPW | BONANZA - BONANZA TAP 161KV | 55261 BONANZT5 161 to 53126 BONANZA5 161 CKT 1 | 177 | 101.562 | 101.9273 | AES - TARBY 161KV | 55262 AES 5 161 to 55264 TARBY 5 161 CKT 1 | 0 | May Limit Renewal Rights
10SP | OKGE | OKGE | RENO - SUNNYLANE 69KV | 54980 SUNNYLN2 69 to 54972 RENO 2 69 CKT 1 | 96 | 101.3147 | 105.0903 | KENTUCKY TAP - SAGE 69KV | 54977 KENTUKT2 69 to 54978 SAGE 2 69 CKT 1 | 0 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 493 | 99.0941 | 127.9686 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 39 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54934 DRAPER 7 345 WND 2 DRAPER 4 2 | 493 | 99.0941 | 127.9686 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 39 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 1 | 54933 DRAPER 4 138 WND 1 DRAPER 3 1 | 493 | 96.0646 | 122.4304 | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55721 DRAPER2113.8 CKT 2 | 172 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | DRAPER 345/138KV TRANSFORMER CKT 2 | 54933 DRAPER 4 138 WND 1 DRAPER 4 2 | 493 | 96.0646 | 122.4304 | 54934 DRAPER 7 345 WND 2 DRAPER 3 1 | 54933 DRAPER 4 138 to 54934 DRAPER 7 345 to 55720 DRAPER1113.8 CKT 1 | 172 | Add third 345 - 138 kV transformer at Draper in 2008 at OKGE expense and May be relieved by operating directive until 2008.
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 95.8778 | 104.9132 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 436 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55100 PAOLI- 4 138 WND 2 PAOLI 1 1 | 50 | 95.6972 | 104.7331 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 455 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 87.1262 | 121.7318 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 474 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 85.342 | 117.5336 | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55743 NORTWS2113.8 CKT 2 | 554 | Solution Undetermined
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 94.1271 | 102.9134 | CHIGLEY - WYNNEWOOD TAP 138KV CKT 1 | 55114 CHIGLEY4 138 to 55122 WYNNTAP4 138 CKT 1 | 625 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | PAOLI 138/69KV TRANSFORMER | 55099 PAOLI 269.0 WND 1 PAOLI 1 1 | 50 | 93.9583 | 102.7465 | CHIGLEY 138/69KV TRANSFORMER CKT 1 | 55113 CHIGLEY269.0 to 55114 CHIGLEY4 138 to 55712 CHIGLEY113.2 CKT 1 | 645 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 59.698 | 124.6808 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 678 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54880 NORTWST7 345 WND 2 NORTWST3 2 | 493 | 79.8215 | 111.6964 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 780 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 53.0211 | 117.7161 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 799 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 54.6448 | 118.2469 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 803 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 31.4521 | 121.2707 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 808 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 71.5328 | 127.4185 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 814 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54908 ARCADIA7 345 WND 2 ARCADIA3 2 | 493 | 53.2699 | 115.2719 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 853 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 53.7333 | 113.6809 | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55704 ARCADI2113.8 CKT 2 | 862 | Solution Undetermined
10SP | OKGE | OKGE | POOST ROAD - SE15TH 138KV | 54993 SE15TH 4 138 to 54965 POSTRDT4 138 CKT 1 | 191 | 50.0418 | 108.3503 | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 863 | May Limit Renewal Rights
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 2 | 54879 NORTWST4 138 WND 1 NORTWST3 2 | 493 | 78.207 | 107.6762 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 876 | Solution Undetermined
10SP | OKGE | OKGE | FOREST HILL - TECUMSEH 69KV | 55071 TECUMSH2 69 to 55074 FRSTHIL2 69 CKT 1 | 72 | 67.2562 | 104.864 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 889 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 18.1604 | 118.3791 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 890 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 2 | 54907 ARCADIA4 138 WND 1 ARCADIA3 2 | 493 | 52.3616 | 110.6931 | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 to 54908 ARCADIA7 345 to 55703 ARCADI1113.8 CKT 1 | 919 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 71.8831 | 115.4932 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 921 | Solution Undetermined
10SP | OKGE | OKGE | MISSION HILL - SHAWNEE 69KV | 55070 MISSION2 69 to 55068 SHAWNEE2 69 CKT 1 | 51 | 52.1042 | 103.6705 | FOREST HILL - SQUIRL CREEK 138KV | 55059 SQUIRCK4 138 to 55075 FRSTHIL4 138 CKT 1 | 953 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 19.2762 | 110.4536 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 971 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 287 | 85.7633 | 103.0908 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 975 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 69.3561 | 109.766 | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 983 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 53.1716 | 102.1109 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 986 | May Limit Renewal Rights
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 55.2572 | 104.23 | DIVISION AVE - LAKESIDE 138KV | 54849 LAKESID4 138 to 54853 DVISION4 138 CKT 1 | 996 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 24.658 | 113.6249 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 1018 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 24.607 | 113.3968 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 1021 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 52.1422 | 111.2659 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1042 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #5 138KV | 54990 TINKER24 138 to 54994 TINKER54 138 CKT 1 | 191 | 78.8769 | 101.916 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1052 | May Limit Renewal Rights
10SP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54941 HSL 4 138 CKT 1 | 287 | 6.4899 | 107.2527 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1055 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 40.9021 | 105.1312 | EASTERN AVE - MEMORIAL 138KV | 54832 EASTERN4 138 to 54835 MEMRIAL4 138 CKT 1 | 1057 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 53.2497 | 109.4846 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1059 | Solution Undetermined
10SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 67.9261 | 103.7393 | NORTHWEST - PANTHER 138KV | 54854 BRADEN 4 138 to 54879 NORTWST4 138 CKT 1 | 1074 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - SILVER LAKE 138KV | 54853 DVISION4 138 to 54852 SLVRLAK4 138 CKT 1 | 287 | 61.1921 | 105.868 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1090 | Solution Undetermined
10SP | OKGE | OKGE | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 287 | 47.412 | 103.9447 | DIVISION AVE - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54853 DVISION4 138 CKT 1 | 1093 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 287 | 40.916 | 109.5389 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1094 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54880 NORTWST7 345 WND 2 NORTWST2 1 | 493 | 69.2342 | 102.9968 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1094 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54908 ARCADIA7 345 WND 2 ARCADIA2 1 | 493 | 40.9803 | 104.5009 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1101 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 64.4361 | 104.3234 | CZECH HALL - XEROX 138KV | 54893 XEROX 4 138 to 54894 CZECHAL4 138 CKT 1 | 1101 | Solution Undetermined
10SP | OKGE | OKGE | LONEOAK - QUAIL CREEK 138KV | 54851 QUAILCK4 138 to 54873 LONEOAK4 138 CKT 1 | 308 | 67.1419 | 102.9211 | PANTHER - SILVER LAKE 138KV | 54852 SLVRLAK4 138 to 54854 BRADEN 4 138 CKT 1 | 1102 | Solution Undetermined
10SP | OKGE | OKGE | CZECH HALL - XEROX 138KV | 54894 CZECHAL4 138 to 54893 XEROX 4 138 CKT 1 | 382 | 61.0675 | 103.977 | MCCLAIN - PLEASANT VALLEY 138KV | 54902 MCCLAIN4 138 to 54929 PLVALLY4 138 CKT 1 | 1126 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 18.5269 | 102.2975 | DANFORTH - OMPA-EDMOND HAFER 138KV | 54833 DANFRTH4 138 to 56174 OMHAFER4 138 CKT 1 | 1138 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 57.8075 | 103.2932 | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 1142 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 47.6454 | 103.6795 | PLEASANT VALLEY - SOUTHGATE 138KV | 54928 SOGATE 4 138 to 54929 PLVALLY4 138 CKT 1 | 1148 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 17.5745 | 101.5186 | FOREST HILL - MAUD 138KV | 55055 MAUD 4 138 to 55075 FRSTHIL4 138 CKT 1 | 1155 | Solution Undetermined
10SP | OKGE | OKGE | HEFNER - TULSA 138KV | 54847 TULSA 4 138 to 54848 HEFNER 4 138 CKT 1 | 222 | 80.9743 | 100.9953 | 84TH ST - TENNESSEE TAP 138KV | 54837 TENESTP4 138 to 54843 84TH ST4 138 CKT 1 | 1158 | May Limit Renewal Rights and May be a problem in the 06SP
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 62.1764 | 101.6976 | MORGAN - XEROX 138KV | 54893 XEROX 4 138 to 54896 MORGAN 4 138 CKT 1 | 1160 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 58.5198 | 101.9059 | CIMARRON - HAYMAKER 138KV | 54863 HAYMAKR4 138 to 54898 CIMARON4 138 CKT 1 | 1165 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA 345/138KV TRANSFORMER CKT 1 | 54907 ARCADIA4 138 WND 1 ARCADIA2 1 | 493 | 40.5542 | 101.242 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1170 | Solution Undetermined
10SP | OKGE | OKGE | CIMARRON - CZECH HALL 138KV | 54894 CZECHAL4 138 to 54898 CIMARON4 138 CKT 1 | 382 | 49.6952 | 102.1542 | DIVISION AVE - MUSTANG 138KV | 54853 DVISION4 138 to 54861 MUSTANG4 138 CKT 1 | 1170 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 17.0043 | 100.703 | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 1181 | Solution Undetermined
10SP | OKGE | OKGE | REMNGTON PARK - STONEWALL 138KV | 54870 STONWAL4 138 to 54872 REMPKTP4 138 CKT 1 | 191 | 72.3203 | 100.9389 | MEMORIAL - TENNESSEE TAP 138KV | 54835 MEMRIAL4 138 to 54837 TENESTP4 138 CKT 1 | 1182 | Solution Undetermined
10SP | OKGE | OKGE | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 WND 1 NORTWST2 1 | 493 | 68.1865 | 100.3717 | CIMARRON - NORTHWEST 345KV | 54880 NORTWST7 345 to 54901 CIMARON7 345 CKT 1 | 1185 | Solution Undetermined
10SP | OKGE | OMPA | EASTERN AVE - OMPA-EDMOND HAFER 138KV | 54832 EASTERN4 138 to 56174 OMHAFER4 138 CKT 1 | 287 | 47.0403 | 100.3566 | MEMORIAL - SKYLINE 138KV | 54835 MEMRIAL4 138 to 54850 SKYLINE4 138 CKT 1 | 1190 | Solution Undetermined
10SP | OKGE | OKGE | MORGAN - MUSTANG 138KV | 54896 MORGAN 4 138 to 54861 MUSTANG4 138 CKT 1 | 287 | 44.55 | 100.6788 | NORTHWEST 345/138KV TRANSFORMER CKT 1 | 54879 NORTWST4 138 to 54880 NORTWST7 345 to 55742 NORTWS1113.8 CKT 1 | 1190 | Solution Undetermined
10SP | OKGE | OKGE | DIVISION AVE - HAYMAKER 138KV | 54853 DVISION4 138 to 54863 HAYMAKR4 138 CKT 1 | 287 | 60.8821 | 100.2602 | MORGAN - MUSTANG 138KV | 54861 MUSTANG4 138 to 54896 MORGAN 4 138 CKT 1 | 1194 | Solution Undetermined
10SP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54907 ARCADIA4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 15.8339 | 100.0934 | DRAPER LAKE - POOST ROAD 138KV | 54933 DRAPER 4 138 to 54965 POSTRDT4 138 CKT 1 | 1196 | Solution Undetermined
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 71.6775 | 158.7997 | POOST ROAD - SE15TH 138KV | 54965 POSTRDT4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10SP | OKGE | OKGE | TINKER #2 - TINKER #4 138KV | 54990 TINKER24 138 to 54988 TINKER44 138 CKT 1 | 100 | 118.686 | 158.7968 | GLENDALE - SE15TH 138KV | 54986 GLENDAL4 138 to 54993 SE15TH 4 138 CKT 1 | 1200 | Not a valid Overload; Relays trip to open UG transmission line when loading reaches 100%, No problem exist with line open.
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 2 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 2 | 1195 | 31.6609 | 116.8354 | ARCADIA - REDBUD 345KV CKT 1 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 1 | 965 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - REDBUD 345KV CKT 1 | 54909 REDBUD 7 345 to 54908 ARCADIA7 345 CKT 1 | 1195 | 31.5953 | 116.592 | ARCADIA - REDBUD 345KV CKT 2 | 54908 ARCADIA7 345 to 54909 REDBUD 7 345 CKT 2 | 968 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 36.2624 | 108.3784 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1006 | Solution Undetermined
10WP | OKGE | OKGE | ARCADIA - KAMO MEMORIAL 138KV | 54906 KAMOMEM4 138 to 54907 ARCADIA4 138 CKT 1 | 287 | 44.544 | 104.7573 | ARCADIA - DANFORTH 138KV | 54833 DANFRTH4 138 to 54907 ARCADIA4 138 CKT 1 | 1057 | Solution Undetermined
10WP | OKGE | OKGE | HORSESHOE LAKE - KAMO MEMORIAL 138KV | 54941 HSL 4 138 to 54906 KAMOMEM4 138 CKT 1 | 287 | 30.716 | 101.7165 | ARCADIA - NORTHWEST 345KV | 54880 NORTWST7 345 to 54908 ARCADIA7 345 CKT 1 | 1158 | Solution Undetermined
[11 empty] | Total Cost | 0